## Sheet1
DIESEL FIRE PUMP WEEKLY INPECTION AND TEST
NAME OF INSPECTOR |  | DATE AND TIME
PRE-OPERATION CHECKS
PUMP HOUSE CHECKS |  | FIRE PUMP PROPER CHECKS
BUILDING HEAT >40F | BUILDING HEAT >40F | SUCTION/DISCHARGE/BYPASS OPEN | SUCTION/DISCHARGE/BYPASS OPEN
LOUVERS OPERATIONAL | LOUVERS OPERATIONAL | NO LEAKS IN PIPES | NO LEAKS IN PIPES
NO WATER ON FLOOR | NO WATER ON FLOOR | SUCTION/DISCHARGE GUAGE OKAY | SUCTION/DISCHARGE GUAGE OKAY
COUPLING GUARD INPLACE | COUPLING GUARD INPLACE | WATERFLOW TEST VALVES SHUT | WATERFLOW TEST VALVES SHUT
|  | WATER TO HOSE CONNECTION SHUT | WATER TO HOSE CONNECTION SHUT
DIESEL ENGINE CHECKS
FUEL TANK >2/3 FULL |  | CONTROLLER SELCTOR SWITCH IN AUTO
BATTERY VOLTAGES ARE OKAY |  | BATTERY CHARGING CURRENT OKAY
BATTERY CHARGER NO ALARM LIGHTS |  | ENGINE RUN TIME ________ HOURS
OIL LEVEL IS OKAY |  | COOLING WATER LEVEL OKAY
BATTERY TERMINALS OKAY |  | ELECTROLYTE WATER LEVEL OKAY
WATER-JACKET HEATER IS OKAY
OPERATIONAL CHECKS
SUCTION PRESSURE ________PSI |  | CRANKING TO FULL SPEED TIME OKAY
DISCHARGE PRESSURE________PSI |  | ENGINE OIL PRESSURE ______PSI
PUMP PACKING HAS SLIGHT DISCHARGE* |  | ENGINE SPEED_______RPM
CHECK FOR UNUSUAL NOISE OR VIBRATION |  | ENGINE WATER TEMPERTURE_______F
INPECT PACKING BOXES, BEARINGS, AND PUMP CASING FOR OVERHEATING |  | ENGINE OIL TEMPERTURE _______F
COOLING WATER FLOW INDICATION OKAY
VISUALLY VERIFY NO OPACITY OR PLUME FROM EXHAUST STACK DURING OPERAITON
*ADJUST AS NEEDED
PROCEDURE
1. In the Diesel Fire Pump Building, verify the following prior to starting test:
1. Oil level
2. Jacket heater is on, and engine is warm
3. Battery chargers and battery voltage is ok
4. Cooling water valves are lined up normal
5. Verify Raw Water level and valves are lined up to the pump.
3. Notify Control Room that you are going to start the Diesel Fire Pump
4. Press the spigot icon on the controller and this will start the pump and 30 minute timer.
5. With Diesel Fire Pump running, ensure good oil pressure and coolant flow
6. Monitor water flow through overspeed relief valve (Should Be None) and engine heat exhanger.
7. After 30-minute timer is complete, verify diesel fire pump shuts off.
8. Notify Control Room that test complete and all pumps are back in auto.