## Sheet1
ELECTRIC AND JOCKEY FIRE PUMP MONTHLY INPECTION AND TEST |  |  |  | PROCEDURE
NAME OF INSPECTOR |  | DATE AND TIME |  |  | 1. PERFORM PRE-OPERATION CHECKS
2. VERIFY RAW WATER TANK LEVEL AND ISOLATION VALVES ARE PROPER LEVEL AND POSITIONS
PRE-OPERATION CHECKS |  |  |  |  | 3. START JOCKEY PUMP BY SLOWLY BLEEDING OFF PRESSURE AT JOCK PUMP CONTROLER SENSIN LINES
PUMP HOUSE CHECKS |  | FIRE PUMP PROPER CHECKS |  |  | 4. CLOSE SENSING LINES AND VERFIFY JOCKEY PUMP STOPS
BUILDING HEAT >40F | BUILDING HEAT >40F | SUCTION/DISCHARGE OPEN | SUCTION/DISCHARGE/BYPASS OPEN |  | 5. START THE ENGINE FIRE PUMP BY DEPRESSING THE SPIGOT ICON PUSHBUTTON ON CONTROLLER
LOUVERS OPERATIONAL | LOUVERS OPERATIONAL | NO LEAKS IN PIPES | NO LEAKS IN PIPES |  | 6. OBSERVE MOTOR COMING UP TO SPEED AND RECORD MAX CURRENT
NO WATER ON FLOOR | NO WATER ON FLOOR | SUCTION/DISCHARGE GUAGE OKAY | SUCTION/DISCHARGE GUAGE OKAY |  | 7. MONITOR SLIGHT WATER FLOW THROUGH RELIEF VALVE
COUPLING GUARD INPLACE | COUPLING GUARD INPLACE | WATER FLOW TEST VALVES SHUT | WATERFLOW TEST VALVES SHUT |  | 8. RECORD OPERATION CHECKS
|  | WATER TO HOSE CONNECTION SHUT | WATER TO HOSE CONNECTION SHUT |  | 9. VERIFY ENGINE SHUTS DOWN AUTOMATICLY AFTER 10 MINUTES
FIRE PUMP CHECKS
JOCKEY PUMP CONTROLER ON & OKAY |  | VERIFY SPACE HEATER IS ON/MOTOR WARM
ELECTRIC FIRE PUMP CONTROLER ON W/NO ALARMS |  | PHASE VOLTAGE A:_____B:_____C:_____
SYSTEM PRESSURE _______PSI
OPERATIONAL CHECKS
SUCTION PRESSURE ________PSI |  | MOTOR RAMP TO FULL SPEED TIME OKAY
DISCHARGE PRESSURE________PSI |  | VERIFY SLIGHT FLOW ON RELIEF VALVE
PUMP PACKING HAS SLIGHT DISCHARGE* |  | PHASE VOLTAGE A:_____B:_____C:_____
CHECK FOR UNUSUAL NOISE OR VIBRATION |  | PHASE CURRENT A:_____B:_____C:_____
INPECT PACKING BOXES, BEARINGS, AND PUMP CASING FOR OVERHEATING |  | SYSTEM PRESSURE _______PSI
STARTING CURRENT HIGHEST PHASE ______AMPS
*ADJUST AS NEEDED