## Sheet1
Alarm List (Excel)
Jackson Generation
Report generated on Thursday, May 21, 2026 at 5/21/2026 8:07:44 PM
Status: OPEN; Site: Jackson Generation
Results: 42
Alarm ID | Description | Loc/Asset | Site | Manual Alarm? | Condition | Technology | Date Created | Closed? | WO Required | WO Number | Task | Last Comment | Recommendation | Age (days)
17 | Probe vacuum VG1A (<10 inch HG); -2.5 | UNIT 1 CEMS UNIT 1 CEMS (01-CEMS) | Jackson Generation | No | NORMAL |  | 2022-05-01 13:29 | No | No |  | Unit 1 Daily CEMS | John Noble 11/10/2022 09:53:34 Unit off |  | 1481
18 | Probe vacuum VG1b (<10 inch HG); -1.5 | UNIT 1 CEMS UNIT 1 CEMS (01-CEMS) | Jackson Generation | No | NORMAL |  | 2022-05-01 13:29 | No | No |  | Unit 1 Daily CEMS | Justin Wandahovich 01/17/2025 06:27:49 Old Al’s |  | 1481
19 | CONV TEMP (315 +/- 5 DEG C) - NOx/NH3; RESPONSE: 700; HI: > 320 DEG C ; LO: < 310 DEG C | UNIT 1 CEMS UNIT 1 CEMS (01-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 1 Weekly CEMS |  |  | 1481
20 | NO OFFSET (50 TO 150 MV) - NOX/O2; RESPONSE: 0; HI: > 150 MV ; LO: < 50 MV | UNIT 1 CEMS UNIT 1 CEMS (01-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 1 Weekly CEMS |  |  | 1481
21 | NO OFFSET (50 TO 150 MV) - NOx/NH3; RESPONSE: 0; HI: > 150 MV ; LO: < 50 MV | UNIT 1 CEMS UNIT 1 CEMS (01-CEMS) | Jackson Generation | No | NORMAL |  | 2022-05-01 13:29 | No | No |  | Unit 1 Weekly CEMS |  |  | 1481
22 | NOx OFFSET (50 TO 150 mV) - NOX/O2; RESPONSE: 1.8; HI: > 150 mV ; LO: < 50 mV | UNIT 1 CEMS UNIT 1 CEMS (01-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 1 Weekly CEMS |  |  | 1481
23 | NOx OFFSET (50 TO 150 mV) - NOx/NH3; RESPONSE: 1.3; HI: > 150 ; LO: < 50 | UNIT 1 CEMS UNIT 1 CEMS (01-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 1 Weekly CEMS |  |  | 1481
24 | PMT SIGNAL -ETEST (2000 =/- 1000 mV); RESPONSE: -3; HI: > 3000 mV ; LO: < 1000 mV | UNIT 1 CEMS UNIT 1 CEMS (01-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 1 Weekly CEMS |  |  | 1481
27 | Probe vacuum VG1A (<10 inch HG); -.5 | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | NORMAL |  | 2022-05-01 13:29 | No | No |  | Unit 2 Daily CEMS | John Noble 11/10/2022 09:38:57 Units off |  | 1481
28 | Probe vacuum VG1b (<10 inch HG); -1.0 | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | NORMAL |  | 2022-05-01 13:29 | No | No |  | Unit 2 Daily CEMS | John Noble 04/10/2023 08:55:36 |  | 1481
29 | CONV TEMP (315 +/- 5 DEG C) - NOx/NH3; RESPONSE: 700; HI: > 320 DEG C ; LO: < 310 DEG C | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 2 Weekly CEMS |  |  | 1481
30 | NO OFFSET (50 TO 150 MV) - NOX/O2; RESPONSE: 0; HI: > 150 MV ; LO: < 50 MV | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 2 Weekly CEMS |  |  | 1481
31 | NO OFFSET (50 TO 150 MV) - NOx/NH3; RESPONSE: 0; HI: > 150 MV ; LO: < 50 MV | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | NORMAL |  | 2022-05-01 13:29 | No | No |  | Unit 2 Weekly CEMS |  |  | 1481
32 | NO SLOPE (1.0 TP 0.3) - NOX/O2; RESPONSE: 1.013; HI: > 1 ; LO: < .3 | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 2 Weekly CEMS |  |  | 1481
33 | NOx OFFSET (50 TO 150 mV) - NOX/O2; RESPONSE: 1.4; HI: > 150 mV ; LO: < 50 mV | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 2 Weekly CEMS |  |  | 1481
34 | NOx OFFSET (50 TO 150 mV) - NOx/NH3; RESPONSE: 1.1; HI: > 150 ; LO: < 50 | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 2 Weekly CEMS |  |  | 1481
35 | PMT AT SPAN GAS CONC (0 TO 5000 mV); RESPONSE: -3.5; HI: > 5000 mV ; LO: < 0 mV | UNIT 2 CEMS UNIT 2 CEMS (02-CEMS) | Jackson Generation | No | PENDING |  | 2022-05-01 13:29 | No | No |  | Unit 2 Weekly CEMS |  |  | 1481
36 | Check all Unit trans containment berms for H2O level; RESPONSE: Unsat; COMMENT: water in sump U1 UAT and GSU | BOP TRANSFORMER | Jackson Generation | No | PENDING |  | 2022-05-01 16:18 | No | No |  | Weekly Operational Checks/Transformer Readings | Quinton Amerson 05/01/2022 16:13:05 water in sump U1 UAT and GSU |  | 1481
154 | VCND 191/320/118/100 Strainer Vent valves (4); RESPONSE: Closed | Steam Cycle Drains Condensate System Condensate Pump "A" | Jackson Generation | No | NORMAL |  | 2022-05-18 03:26 | No | No |  | U1 Drains |  |  | 1464
155 | 154/360/135/129 Strainer Vent valves (4); RESPONSE: Closed | Steam Cycle Drains Condensate System Condensate Pump "B" | Jackson Generation | No | NORMAL |  | 2022-05-18 03:26 | No | No |  | U1 Drains |  |  | 1464
156 | VCND 330/133/168/165 Strainer Vent valves (4); RESPONSE: Closed | Steam Cycle Drains Condensate System Condensate Pump "C" | Jackson Generation | No | NORMAL |  | 2022-05-18 03:26 | No | No |  | U1 Drains |  |  | 1464
186 | Seal Water Pressure; RESPONSE: 0; COMMENT: No gauges | UNIT 1 CONDENSATE | Jackson Generation | Yes | PENDING |  | 2022-05-25 10:05 | No | No |  | Unit 1 Outside Rounds | Danil Klokov 05/24/2022 22:13:52 No gauges |  | 1457
248 | Seal Water Pressure; RESPONSE: 0; COMMENT: No gauges | UNIT 2 CONDENSATE | Jackson Generation | Yes | PENDING |  | 2022-05-29 03:16 | No | No |  | Unit 2 Outside Rounds | Eugene Mykhailenko 05/29/2022 00:20:45 No gauges |  | 1453
900 | COUPLING GUARD INPLACE; RESPONSE: Unsat | BOP FIRE PROTECTION SYSTEM ELECTRIC FIRE PUMP (00-FPS-PMP-01) | Jackson Generation | No | PENDING |  | 2022-08-14 08:39 | No | No |  | Electric and Jockey Fire Pump Monthly Inspection and Test |  |  | 1376
8294 | LP Drum pH; 9.99; HI: > 9.8 ; LO: < 9.5 | Water Chemistry | Jackson Generation | No | NORMAL |  | 2025-01-20 14:54 | No | No |  | U1 Water Chemistry |  |  | 486
8296 | LP Drum pH; 10.01; HI: > 9.8 ; LO: < 9.5 | Water Chemistry | Jackson Generation | No | NORMAL |  | 2025-01-20 14:54 | No | No |  | U2 Water Chemistry |  |  | 486
8339 | CND After Chem Feed Silica; 8; HI: > 5 ppb | Water Chemistry | Jackson Generation | No | MARGINAL |  | 2025-01-24 10:02 | No | No |  | U2 Water Chemistry |  |  | 482
8340 | HP Drum pH; 9.78; HI: > 9.5 ; LO: < 9.2 | Water Chemistry | Jackson Generation | No | NORMAL |  | 2025-01-24 10:02 | No | No |  | U2 Water Chemistry |  |  | 482
8341 | CND After Chem Feed pH; 10.12; HI: > 10 ; LO: < 9.6 | Water Chemistry | Jackson Generation | No | NORMAL |  | 2025-01-24 10:02 | No | No |  | U2 Water Chemistry |  |  | 482
8370 | HP Drum Iron; 14; HI: > 10 ppb | Water Chemistry | Jackson Generation | No | MARGINAL |  | 2025-01-27 07:16 | No | No |  | U2 Water Chemistry |  |  | 479
10840 | Fuel Level (>90%); 70; LO: < 90 | UNIT 1 ACC EDG (01-EDG) | Jackson Generation | No | NORMAL |  | 2025-12-10 10:36 | No | No |  | BOP | Juan Silva 12/14/2025 19:50:11 Indoor temp low limit |  | 162
11557 | ST Drains Sump Pump Panel/Alarms; Unsat; COMMENT: LOTO | UNIT 2 WASTE WATER COLLECTION ST DRAINS TANK SUMP PUMP 1A 02-PDR-PMP-01A (02-PDR-PMP-01A) | Jackson Generation | No | PENDING |  | 2026-04-26 20:43 | No | No |  | Unit 2 Outside Rounds | Rigo Garcia 05/21/2026 08:27:43 LOTO |  | 25
11631 | Fan condition (sound, vibration, cleanness); Unsat; COMMENT: Fan LOTO motor removed | UNIT 1 CLOSED COOLING WATER AIR COOLED HEAT EXCHANGER FAN 05B (01-CCW-FAN-05B) | Jackson Generation | No | PENDING |  | 2026-05-09 11:15 | No | No |  | Weekly Operational Checks/Transformer Readings | John Noble 05/09/2026 08:57:09 Fan LOTO motor removed |  | 12
11694 | Abnormal Conditions/Leaks; Unsat | UNIT 2 FUEL GAS FUEL GAS PERFORMANCE HEATER 02-FGS-HEX-01 (02-FGS-HEX-01) | Jackson Generation | No | PENDING |  | 2026-05-16 11:33 | No | No |  | Unit 2 Outside Rounds | Eugene Mykhailenko 05/16/2026 10:39:49 SR |  | 5
11697 | Diesel Tank Level (>75%); 65; LO: < 75 % | BOP FIRE PROTECTION SYSTEM | Jackson Generation | No | PENDING |  | 2026-05-17 16:52 | No | No |  | BOP | Eugene Mykhailenko 05/17/2026 06:17:28 Need to order |  | 4
11714 | Chem Tank Level - Anti Scalant; 10; HI: < 25 % | UNIT 1 DEMINERALIZED WATER | Jackson Generation | No | PENDING |  | 2026-05-19 13:07 | No | No |  | BOP |  |  | 2
11718 | Visual Steam/Water Leaks; Unsat | UNIT 2 HRSG | Jackson Generation | No | PENDING |  | 2026-05-19 22:16 | No | No |  | Unit 2 Outside Rounds | Juan Silva 05/20/2026 19:19:38 Made some flow adjustments |  | 2
11720 | Active Alarms; Yes | BOP GAS TURBINE GT IGNITION EXCITOR (MBM01GU001) | Jackson Generation | No | PENDING |  | 2026-05-19 22:16 | No | No |  | Unit 2 Outside Rounds | Juan Silva 05/19/2026 19:42:51 SFC smoke alarm back in |  | 2
11725 | Seal Oil/H2 DP (8 PSI); 9.19; HI: > 9 PSI ; LO: < 7.8 PSI | UNIT 2 SEAL OIL | Jackson Generation | No | NORMAL |  | 2026-05-20 21:04 | No | No |  | Unit 2 Outside Rounds | Juan Silva 05/20/2026 19:58:25 High |  | 1
11727 | Alarms; Yes; COMMENT: Ac drain | BOP INSTRUMENT AIR AIR COMPRESSOR 1B (00-INA-CMP-01B) | Jackson Generation | No | NORMAL |  | 2026-05-21 11:21 | No | No |  | BOP | Geovanny Martinez 05/21/2026 11:17:03 Ac drain |  | 0
11728 | Hydrogen flow to purity meter (500); Unsat; COMMENT: Unit down | UNIT 1 GENERATOR | Jackson Generation | No | NORMAL |  | 2026-05-21 11:21 | No | No |  | Unit 1 Outside Rounds | Geovanny Martinez 05/21/2026 10:59:25 Unit down |  | 0
11730 | Oil System Active alarms; Yes; COMMENT: Low oil level Unit is offline | Control Room Checks TCS Lube Oil System | Jackson Generation | No | NORMAL |  | 2026-05-21 17:58 | No | No |  | CRO checklist | Adam Bunker 05/21/2026 17:50:03 Low oil level Unit is offline |  | 0