## BOP
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | Original ID | P&ID
00-FCV-DWS111 | PUMP MIN RECIRC | 00-2"-DWS6017-1BCA2A-1.0 "MOH | 2" | Globe control valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.3 |  | 1 | PD-410
00-FCV-SWS101 | POTABLE WATER MAKEUP CV | 00-4"-SWS6074-1BAH1A-1.0 "MOH | 4" | Ball control valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 80 | 115 | S-STD | 1.0 " | Yes | 94.03.68.100.02.5 |  | 2 | PD-390
00-FCV-SWS112 | SERVICE WATER PUMP RECIRC CONTROL VALVE | 00-4"-SWS6076-1BAH1A-1.0 "MOH | 4" | Globe control valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.100.02.4 |  | 3 | PD-391
00-PCV-AXS113 | AUX BOILER BACK PRESSURE CONTROL VALVE | 00-6"-AXS6500-1DAA1A-2.0 "EIC | 6" | Ball control valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 2.0 " | No | 94.03.68.100.02.1 |  | 4 | PD-120
00-PRV-CMG603 | NITROGEN STORAGE CYLINDER RACK OUTLET | 00-1"-CMG6201-1BCA1A | 1" | Self contained press red reg | CMG | 1BCA1A | NITROGEN | CL600 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.100.02.2 |  | 5 | PD-570
00-PRV-CMG604 | NITROGEN STORAGE CYLINDER RACK OUTLET | 00-1"-CMG6101-1BCA1A | 1" | Self contained press red reg | CMG | 1BCA1A | NITROGEN | CL600 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.100.02.2 |  | 6 | PD-570
00-PRV-INA220 | UTS PRV | 00-0.75"-INA6083-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 7 | PD-552
00-PRV-INA224 | UTS PRV | 00-0.75"-INA6084-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 8 | PD-552
00-PRV-INA228 | UTS PRV | 00-0.75"-INA6085-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 9 | PD-552
00-PRV-INA232 | UTS PRV | 00-0.75"-INA6089-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 10 | PD-552
00-PRV-INA236 | UTS PRV | 00-0.75"-INA6087-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 11 | PD-552
00-PRV-INA240 | UTS PRV | 00-0.75"-INA6091-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 12 | PD-552
00-PRV-INA244 | UTS PRV | 00-0.75"-INA6039-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 13 | PD-553
00-PRV-INA248 | UTS PRV | 00-0.75"-INA6035-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 14 | PD-554
00-PRV-INA252 | UTS PRV | 00-0.75"-INA6033-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 15 | PD-554
00-PRV-INA256 | UTS PRV | 00-0.75"-INA6029-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 16 | PD-554
00-PRV-INA260 | UTS PRV | 00-0.75"-INA6037-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 17 | PD-553
00-PRV-INA264 | UTS PRV | 00-0.75"-INA6043-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 18 | PD-553
00-PRV-INA268 | UTS PRV | 00-0.75"-INA6095-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 19 | PD-553
00-PRV-INA272 | UTS PRV | 00-0.75"-INA6055-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 20 | PD-554
00-PRV-INA276 | UTS PRV | 00-0.75"-INA6057-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 21 | PD-554
00-PRV-INA280 | UTS PRV | 00-0.75"-INA6059-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 22 | PD-554
00-PRV-INA284 | UTS PRV | 00-0.75"-INA6061-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 23 | PD-554
00-PRV-INA288 | UTS PRV | 00-0.75"-INA6063-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 24 | PD-554
00-PRV-INA300 | UTS PRV | 00-0.75"-INA7011-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 25 | PD-555
00-PRV-INA304 | UTS PRV | 00-0.75"-INA6047-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 26 | PD-555
00-PRV-INA308 | UTS PRV | 00-0.75"-INA6051-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 27 | PD-555
00-PRV-INA312 | UTS PRV | 00-0.75"-INA6053-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 28 | PD-555
00-PRV-INA316 | UTS PRV | 00-0.75"-INA6007-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 29 | PD-561
00-PRV-INA320 | UTS PRV | 00-0.75"-INA6003-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 30 | PD-562
00-PRV-INA324 | UTS PRV | 00-0.75"-INA6001-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 31 | PD-562
00-PRV-INA328 | UTS PRV | 00-0.75"-INA6025-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 32 | PD-556
00-PRV-INA332 | UTS PRV | 00-0.75"-INA6027-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 33 | PD-556
00-PRV-INA336 | UTS PRV | 00-0.75"-INA6023-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 34 | PD-556
00-PRV-INA340 | UTS PRV | 00-0.75"-INA6011-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 35 | PD-556
00-PRV-INA344 | UTS PRV | 00-0.75"-INA6017-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 36 | PD-556
00-PRV-INA348 | UTS PRV | 00-0.75"-INA6013-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 37 | PD-556
00-PRV-INA352 | UTS PRV | 00-0.75"-INA6032-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 38 | PD-556
00-PRV-INA356 | UTS PRV | 00-0.75"-INA6009-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 39 | PD-556
00-PRV-INA357 | UTS PRV | 00-0.75"-INA6021-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 40 | PD-556
00-PRV-INA364 | UTS PRV | 00-0.75"-INA6097-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 41 | PD-557
00-PRV-INA368 | UTS PRV | 00-0.75"-INA6099-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 42 | PD-557
00-PRV-INA400 | UTS PRV | 00-0.75"-INA6067-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 43 | PD-557
00-PRV-INA404 | UTS PRV | 00-0.75"-INA6069-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 44 | PD-557
00-PRV-INA408 | UTS PRV | 00-0.75"-INA6065-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 45 | PD-557
00-PRV-INA412 | UTS PRV | 00-0.75"-INA6071-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 46 | PD-557
00-PRV-INA416 | UTS PRV | 00-0.75"-INA6073-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 47 | PD-557
00-PRV-INA420 | UTS PRV | 00-0.75"-INA6081-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 48 | PD-557
00-PRV-INA424 | UTS PRV | 00-0.75"-INA6077-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 49 | PD-557
00-PRV-INA428 | UTS PRV | 00-0.75"-INA6079-1KFD1A | 0.75" | Self contained backpress reg | INA | 1KFD1A | AIR | CL800 | FTE | FTE | 145 | 140 | Type K |  | No | 94.03.68.100.02.2 |  | 50 | PD-557
00-PRV-PWS602 | PRESSURE REFGULATING VALVE FOR EWS 611 | 00-1"-PWS6111-1BCA3A-1.0 "MIC | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | No | 94.03.68.100.02.2 |  | 51 | PD-402
00-PRV-PWS603 | PRESSURE REFGULATING VALVE FOR EWS 612 | 00-1"-PWS6112-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 52 | PD-402
00-PRV-PWS604 | PRESSURE REFGULATING VALVE FOR EWS 613 | 00-1"-PWS6113-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 53 | PD-402
00-PRV-PWS605 | PRESSURE REFGULATING VALVE FOR EWS 614 | 00-1"-PWS6114-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 54 | PD-402
00-PRV-PWS606 | PRESSURE REFGULATING VALVE FOR EWS 615 | 00-1"-PWS6115-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 55 | PD-402
00-PRV-PWS607 | PRESSURE REFGULATING VALVE FOR EWS 616 | 00-1"-PWS6116-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 56 | PD-402
00-PRV-PWS608 | PRESSURE REFGULATING VALVE FOR EWS 617 | 00-1"-PWS6117-1BCA3A-1.0 "MIC | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | No | 94.03.68.100.02.2 |  | 57 | PD-402
00-PRV-PWS609 | PRESSURE REFGULATING VALVE FOR EWS 618 | 00-1"-PWS6118-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 58 | PD-402
00-PRV-PWS610 | PRESSURE REFGULATING VALVE FOR EWS 619 | 00-1"-PWS6119-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 59 | PD-402
00-PRV-PWS629 | PRESSURE REFGULATING VALVE FOR EWS 620 | 00-1"-PWS6120-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 60 | PD-402
00-PRV-PWS630 | PRESSURE REFGULATING VALVE FOR EWS 621 | 00-1"-PWS6121-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 61 | PD-402
00-PRV-PWS631 | PRESSURE REFGULATING VALVE FOR EWS 622 | 00-1"-PWS6122-1BCA3A-1.0 "MIC | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | No | 94.03.68.100.02.2 |  | 62 | PD-402
00-PRV-PWS632 | PRESSURE REFGULATING VALVE FOR EWS 623 | 00-1"-PWS6123-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 63 | PD-402
00-PRV-PWS633 | PRESSURE REFGULATING VALVE FOR EWS 624 & 628 | 00-1"-PWS6124-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 64 | PD-402
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 65 | P&ID
00-PRV-PWS634 | PRESSURE REFGULATING VALVE FOR EWS 625 | 00-1"-PWS6125-1BCA3A-1.0 "MIC | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | No | 94.03.68.100.02.2 |  | 66 | PD-402
00-PRV-PWS635 | PRESSURE REFGULATING VALVE FOR EWS 626 | 00-1"-PWS6126-1BCA3A-1.0 "MOH | 1" | Self contained press red reg | PWS | 1BCA3A | Water | CL150 | RFFE | RFFE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 67 | PD-402
00-PRV-SWS633 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6009-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 68 | PD-392
00-PRV-SWS634 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6021-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 69 | PD-392
00-PRV-SWS635 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6011-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 70 | PD-392
00-PRV-SWS636 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6013-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 71 | PD-392
00-PRV-SWS637 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6016-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 72 | PD-392
00-PRV-SWS638 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6017-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 73 | PD-392
00-PRV-SWS639 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6023-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 74 | PD-392
00-PRV-SWS640 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6027-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 75 | PD-392
00-PRV-SWS641 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6025-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 76 | PD-392
00-PRV-SWS642 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6001-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 77 | PD-392
00-PRV-SWS643 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6003-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 78 | PD-392
00-PRV-SWS644 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6007-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 79 | PD-392
00-PRV-SWS645 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6045-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 80 | PD-393
00-PRV-SWS646 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6047-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 81 | PD-393
00-PRV-SWS647 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6051-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 82 | PD-393
00-PRV-SWS648 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6053-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 83 | PD-393
00-PRV-SWS649 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6055-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 84 | PD-393
00-PRV-SWS650 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6057-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 85 | PD-393
00-PRV-SWS651 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6059-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 86 | PD-393
00-PRV-SWS652 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6061-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 87 | PD-393
00-PRV-SWS653 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6063-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 88 | PD-393
00-PRV-SWS654 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6029-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 89 | PD-393
00-PRV-SWS655 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6035-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 90 | PD-393
00-PRV-SWS656 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6033-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 91 | PD-393
00-PRV-SWS657 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6037-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 92 | PD-394
00-PRV-SWS658 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6039-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 93 | PD-393
00-PRV-SWS659 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6043-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 94 | PD-394
00-PRV-SWS660 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6083-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 95 | PD-394
00-PRV-SWS661 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6084-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 96 | PD-394
00-PRV-SWS662 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6085-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 97 | PD-394
00-PRV-SWS663 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6089-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 98 | PD-394
00-PRV-SWS664 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6087-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 99 | PD-394
00-PRV-SWS665 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6091-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 100 | PD-394
00-PRV-SWS666 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6095-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 101 | PD-394
00-PRV-SWS667 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6097-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 102 | PD-394
00-PRV-SWS668 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6099-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 103 | PD-394
00-PRV-SWS669 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6065-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 104 | PD-394
00-PRV-SWS670 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6067-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 105 | PD-394
00-PRV-SWS671 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6069-1BAB3A | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 |  | No | 94.03.68.100.02.2 |  | 106 | PD-394
00-PRV-SWS672 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6071-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 107 | PD-394
00-PRV-SWS673 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6073-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 108 | PD-394
00-PRV-SWS674 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6081-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 109 | PD-394
00-PRV-SWS675 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6077-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 110 | PD-395
00-PRV-SWS676 | UTILITY STATION PRESSURE REGULATOR | 00-1"-SWS6079-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 111 | PD-395
00-PRV-SWS677 | BEARING FLUSH PRESSURE REGULATOR | 00-1"-SWS6041-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 112 | PD-961
00-PRV-SWS678 | FREE CHLORINE PRESSURE REGULATOR | 00-0.5"-SWS6169-1LCR2A | 0.5" | Self contained press red reg | SWS | 1LCR2A | Water | CL600 | FTE | FTE | 145 | 110 | 0.065" Avg. Wall |  | No | 94.03.68.100.02.2 |  | 113 | PD-391
00-PSV-AQA100 | TANK 1 PSV | 00-2"-AQA6024-1BCD2A | 2" | Angle press relief valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.175.0 |  | 114 | PD-780
00-PSV-AQA200 | TANK 2 PSV | 00-2"-AQA6160-1BCD2A | 2" | Angle press relief valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.175.0 |  | 115 | PD-781
00-PSV-CMG600 | H2 OVERPRESSURE PROTECTION | 00-1"-CMG6000-1BAA2A | 1" | Angle control valve | CMG | 1BAA2A | HYDROGEN | CL600 | RFFE | RFFE | 150 | 115 | S-80 |  | No | 94.03.68.175.2 |  | 116 | PD-571
00-PSV-CMG611 | NITROGEN OVERPRESSURE PROTECTION | 00-1"-CMG6116-1BCA1A | 1" | Angle press relief valve | CMG | 1BCA1A | NITROGEN | CL150 | RFFE | RFFE | 130 | 115 | S-40S |  | No | 94.03.68.175.2 |  | 117 | PD-570
00-PSV-CMG621 | NITROGEN OVERPRESSURE PROTECTION | 00-1"-CMG6003-1BCA1A | 1" | Angle press relief valve | CMG | 1BCA1A | NITROGEN | CL150 | RFFE | RFFE | 130 | 115 | S-40S |  | No | 94.03.68.175.2 |  | 118 | PD-570
00-TV-SWS721 | WASTEWATER QUENCH CONTROL VALVE | 00-2.5"-SWS6030-1BAH1A-1.0 "MOH | 2.5" | Globe control valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.100.02.2 |  | 119 | PD-961
00-VAQA600 | TANK 2 UNLOADING STATION ISOLATION VALVE | 00-2"-AQA6000-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 120 | PD-781
00-VAQA601 | TANK 2 UNLOADING STATION VAPOR RETURN ISOLATION VALVE | 00-1.5"-AQA6012-1BCD2A | 1.5" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 121 | PD-781
00-VAQA602 | AQA TANK 1 DRAIN ISOLATION VALVE | 00-2"-AQA6002-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 122 | PD-780
00-VAQA603 | TANK 2 DRAIN ISOLATION VALVE | 00-2"-AQA6100-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 123 | PD-781
00-VAQA605 | AQA TANK 1 FORWARDING PUMPS ISOLATION VALVE UPSTREAM OF DRAIN | 00-1"-AQA6005-1BCD2A | 1" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 124 | PD-780
00-VAQA606 | TANK 1 FORWARDING PUMPS ISOLATION VALVE DOWNSTREAM OF DRAIN | 00-1"-AQA6005-1BCD2A | 1" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 125 | PD-780
00-VAQA607 | AQA TANK 1 FORWARDING PUMPS DRAIN ISOLATION VALVE | 00-0.75"-AQA6005-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 126 | PD-780
00-VAQA609 | LEVEL GAUGE 109 ISOLATION VALVE | 00-2"-AQA6009-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 127 | PD-780
00-VAQA610 | LEVEL GAUGE 109 ISOLATION VALVE | 00-2"-AQA6027-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 128 | PD-780
00-VAQA611 | TANK 1 UNLOADING STATION ISOLATION VALVE | 00-2"-AQA6001-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 129 | PD-780
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 130 | P&ID
00-VAQA612 | TANK 1 PUMP RECIRC ISOLATION VALVE DOWNSTREAM OF DRAIN | 00-0.75"-AQA6021-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 131 | PD-780
00-VAQA617 | AQA FORWARDING PUMP SKID ISOLATION VALVE | 00-1"-AQA6011-1BCD2A | 1" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 132 | PD-782
00-VAQA621 | TANK 1 PUMP RECIRC ISOLATION VALVE UPSTREAM OF DRAIN | 00-0.75"-AQA6021-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 133 | PD-780
00-VAQA625 | TANK 1 PUMP RECIRC DRAIN ISOLATION VALVE | 00-0.75"-AQA6021-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 134 | PD-780
00-VAQA628 | PIT AQA101 ISOLATION VALVE | 00-2"-AQA6028-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 135 | PD-780
00-VAQA631 | TANK 2 PUMP RECIRC DRAIN ISOLATION VALVE | 00-0.75"-AQA6022-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 136 | PD-781
00-VAQA636 | TANK 1 UNLOADING STATION VAPOR RETURN ISOLATION VALVE | 00-1.5"-AQA6006-1BCD2A | 1.5" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 137 | PD-780
00-VAQA640 | TANK 1 PUMP RECIRC VENT ISOLATION VALVE | 00-0.75"-AQA6021-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 138 | PD-780
00-VAQA643 | TANK 2 FORWARDING PUMPS ISOLATION VALVE UPSTREAM OF DRAIN | 00-1"-AQA6110-1BCD2A | 1" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 139 | PD-781
00-VAQA647 | PIT AQA201 ISOLATION VALVE | 00-2"-AQA6045-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 140 | PD-781
00-VAQA660 | TANK 2 LEVEL GAUGE 209 ISOLATION VALVE | 00-2"-AQA6135-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 141 | PD-781
00-VAQA665 | TANK 2 LEVEL GAUGE 209 ISOLATION VALVE | 00-2"-AQA6065-1BCD2A | 2" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 142 | PD-781
00-VAQA680 | TANK 2 FORWARDING PUMPS ISOLATION VALVE DOWNSTREAM OF DRAIN | 00-1"-AQA6110-1BCD2A | 1" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 143 | PD-781
00-VAQA681 | TANK 2 PUMP RECIRC VENT ISOLATION VALVE | 00-0.75"-AQA6022-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 144 | PD-781
00-VAQA685 | TANK 2 PUMP RECIRC ISOLATION VALVE UPSTREAM OF DRAIN | 00-0.75"-AQA6022-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 145 | PD-781
00-VAQA687 | TANK 2 PUMP RECIRC ISOLATION VALVE DOWNSTREAM OF DRAIN | 00-0.75"-AQA6022-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 146 | PD-781
00-VAQA690 | TANK 2 FORWARDING PUMP LINE DRAIN ISOLATION VALVE | 00-0.75"-AQA6110-1BCD2A | 0.75" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 147 | PD-781
00-VAXS601 | DRAIN | 00-0.75"-AXS6500-1DAA1A-1.5 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 148 | PD-120
00-VAXS602 | DRAIN | 00-0.75"-AXS6762-1BAA2A-1.0 "EIC | 0.75" | Gate valve | AXS | 1BAA2A | Steam/Water | CL800 | SWE | SWE | 15 | 212 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 149 | PD-121
00-VAXS622 | INSTRUMENT | 00-0.75"-AXS6500-1DAA1A-1.5 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.2H |  | 150 | PD-120
00-VAXS623 | BACK PRESSURE CONTROL VALVE ISOLATION | 00-8"-AXS6500-1DAA1A-2.0 "EIC | 8" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 2.0 " | No | 94.03.68.150.03.2H | FLEXIBLE WEDGE, 3-WAY DRAIN | 151 | PD-120
00-VAXS624 | BACK PRESSURE CONTROL VALVE BYPASS | 00-6"-AXS6024-1DAA1A-2.0 "EIC | 6" | Globe valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 2.0 " | No | 94.03.68.150.03.2H | THROTTLING SERVICE | 152 | PD-120
00-VAXS625 | BACK PRESSURE CONTROL VALVE ISOLATION | 00-8"-AXS6500-1DAA1A-2.0 "EIC | 8" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 2.0 " | No | 94.03.68.150.03.2H | FLEXIBLE WEDGE, 3-WAY DRAIN | 153 | PD-120
00-VBDN612 | SWS TANK NOZZLE B2 ISOLATION | 00-8"-BDN6113-1BAA2A-1.0 "MOH | 8" | Butterfly valve | BDN | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 154 | PD-390
00-VBDN613 | BLOWDOWN TO SWS TANK ISOLATION | 00-8"-BDN6113-1BAA2A-1.0 "MOH | 8" | Butterfly valve | BDN | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 155 | PD-091
00-VBDN614 | VENT ROOT VALVE | 00-0.75"-BDN6113-1BAA2A-1.0 "MOH | 0.75" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 156 | PD-091
00-VBDN615 | DRAIN ROOT VALVE | 00-0.75"-BDN6113-1BAA2A-1.0 "MOH | 0.75" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 157 | PD-091
00-VBDN687 | BLOWDOWN TO WDR SUMP ISOLATION | 00-8"-BDN6687-1BAA2A-1.0 "MOH | 8" | Butterfly valve | BDN | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 158 | PD-091
00-VBDN688 | VENT ROOT VALVE | 00-0.75"-BDN6687-1BAA2A-1.0 "MOH | 0.75" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 159 | PD-091
00-VBDN689 | DRAIN ROOT VALVE | 00-0.75"-BDN6687-1BAA2A-1.0 "MOH | 0.75" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 160 | PD-091
00-VCCF102 | AUX BOILER AMMONIA SKID ISOLATION | 00-0.5"-CCF6858-1BCA1A | 0.5" | Ball valve | CCF | 1BCA1A | 19% Aqueous Ammonia | CL600 | SWE | SWE | 15 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 161 | PD-521
00-VCMG600 | VENT | 00-0.75"-CMG6010-1BAA2A | 0.75" | Globe valve | CMG | 1BAA2A | HYDROGEN | CL800 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 162 | PD-571
00-VCMG601 | N2 PURGE CONNECTION | 00-0.75"-CMG6002-1BAA2A | 0.75" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 163 | PD-571
00-VCMG603 | H2 ISOLATION | 00-1.5"-CMG6010-1BAA2A | 1.5" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 164 | PD-571
00-VCMG610 | H2 ISOLATION | 00-1.5"-CMG6010-1BAA2A | 1.5" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 165 | PD-571
00-VCMG619 | INSTRUMENTATION | 00-0.75"-CMG6101-1BCA1A | 0.75" | Globe valve | CMG | 1BCA1A | NITROGEN | CL800 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 166 | PD-570
00-VCMG629 | INSTRUMENTATION | 00-0.75"-CMG6201-1BCA1A | 0.75" | Globe valve | CMG | 1BCA1A | NITROGEN | CL800 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 167 | PD-570
00-VDWS600 | INSTRUMENT | 00-0.75"-DWS6012-1BCA2A-1.0 "MOH | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.3H |  | 168 | PD-410
00-VDWS601 | VENT | 00-0.75"-DWS6050-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.3H |  | 169 | PD-379
00-VDWS605 | TANK ISOLATION | 00-8"-DWS6036-1BCA2A-1.0 "MOH | 8" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 170 | PD-410
00-VDWS613 | CONTROL VALVE ISOLATION | 00-4"-DWS6017-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 171 | PD-410
00-VDWS614 | TANK ISOLATION | 00-4"-DWS6017-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 172 | PD-410
00-VDWS615 | CONTROL VALVE ISOLATION | 00-4"-DWS6017-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 173 | PD-410
00-VDWS616 | CIP TANK ISOLATION | 00-2"-DWS6050-1BCA2A | 2" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 | PISTON | 174 | PD-379
00-VDWS626 | TANK ISOLATION | 00-4"-DWS6026-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 175 | PD-410
00-VDWS628 | DRAIN | 00-0.75"-DWS6017-1BCA2A-1.0 "MOH | 0.75" | Gate valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 | FLEXIBLE WEDGE | 176 | PD-410
00-VDWS631 | VENT | 00-0.75"-DWS6092-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.2H |  | 177 | PD-376
00-VDWS632 | TANK ISOLATION | 00-2"-DWS6032-1BCA2A-1.0 "MOH | 2" | Ball valve | DWS | 1BCA2A | Water | CL600 | RFFE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 178 | PD-410
00-VDWS633 | TANK ISOLATION | 00-2"-DWS6033-1BCA2A-1.0 "MOH | 2" | Ball valve | DWS | 1BCA2A | Water | CL600 | RFFE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 179 | PD-410
00-VDWS634 | CONTROL VALVE BYPASS | 00-2.5"-DWS6034-1BCA2A-1.0 "MOH | 2.5" | Globe valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.03.2H | THROTTLING SERVICE | 180 | PD-410
00-VDWS640 | DRAIN | 00-0.75"-DWS6017-1BCA2A-1.0 "MOH | 0.75" | Gate valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 | FLEXIBLE WEDGE | 181 | PD-410
00-VDWS645 | VENT | 00-0.75"-DWS6017-1BCA2A-1.0 "MOH | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.2H |  | 182 | PD-410
00-VDWS646 | RO SKID A SUPPLY ISOLATION | 00-3"-DWS6037-1BCA2A | 3" | Ball valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S |  | No | 94.03.68.150.03.1 |  | 183 | PD-376
00-VDWS647 | RO SKID B SUPPLY ISOLATION | 00-3"-DWS6092-1BCA2A | 3" | Ball valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S |  | No | 94.03.68.150.03.1 |  | 184 | PD-376
00-VDWS649 | VENT | 00-0.75"-DWS6037-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.2H |  | 185 | PD-376
00-VDWS652 | TANK ISOLATION | 00-6"-DWS6052-1BCA2A-1.0 "MOH | 6" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 186 | PD-410
00-VDWS654 | TANK ISOLATION | 00-8"-DWS6054-1BCA2A-1.0 "MOH | 8" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 187 | PD-410
00-VDWS656 | TANK ISOLATION | 00-3"-DWS6056-1BCA2A-1.0 "MOH | 3" | Gate valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.03.0 |  | 188 | PD-410
00-VDWS658 | TANK ISOLATION | 00-4"-DWS6058-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 189 | PD-410
00-VDWT600 | VENT VALVE | 00-0.75"-DWT6030-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | FTE | 110 | 115 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 190 | PD-376
00-VDWT601 | INSTRUMENT ISOLATION VALVE | 00-0.75"-DWT6015-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | SWE | 145 | 110 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 191 | PD-376
00-VDWT602 | INSTRUMENT ISOLATION VALVE | 00-0.75"-DWT6015-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | SWE | 145 | 110 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 192 | PD-376
00-VDWT603 | DEMIN TRAILER DRAIN/REJECT ISOLATION VALVE | 00-4"-DWT6176-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 193 | PD-378
00-VDWT604 | DEMIN TRAILER DRAIN/REJECT ISOLATION VALVE | 00-4"-DWT6175-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 194 | PD-378
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 195 | P&ID
00-VDWT605 | VENT VALVE | 00-0.75"-DWT6028-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | FTE | 110 | 115 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 196 | PD-376
00-VDWT606 | VENT VALVE | 00-0.75"-DWT6018-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | FTE | 145 | 110 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 197 | PD-376
00-VDWT607 | VENT VALVE | 00-0.75"-DWT6025-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | FTE | 145 | 110 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 198 | PD-376
00-VDWT608 | MIXED BED EFFLUENT HEADER (C/D SIDE) ISOLATION VALVE | 00-4"-DWT6168-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 199 | PD-377
00-VDWT609 | MIXED BED EFFLUENT HEADER (A/B SIDE) ISOLATION VALVE | 00-4"-DWT6168-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 200 | PD-377
00-VDWT610 | MIXED BED C INLET ISOLATION VALVE | 00-4"-DWT6005-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 201 | PD-377
00-VDWT611 | MIXED BED B INLET ISOLATION VALVE | 00-4"-DWT6012-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 202 | PD-377
00-VDWT612 | MIXED BED INTERPASS (A/B SIDE) ISOLATION VALVE | 00-4"-DWT6011-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 203 | PD-377
00-VDWT613 | MIXED BED INTERPASS (C/D SIDE) ISOLATION VALVE | 00-4"-DWT6011-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 204 | PD-377
00-VDWT614 | MIXED BED INTERPASS (A/B SIDE) ISOLATION VALVE | 00-4"-DWT6000-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 205 | PD-377
00-VDWT615 | MIXED BED INTERPASS (C/D SIDE) ISOLATION VALVE | 00-4"-DWT6001-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 206 | PD-377
00-VDWT616 | VENT VALVE | 00-0.75"-DWT6008-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | FTE | 110 | 115 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 207 | PD-377
00-VDWT617 | MIXED BED MANIFOLD INLET ISOLATION VALVE | 00-4"-DWT6019-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 208 | PD-377
00-VDWT620 | MIXED BED INLET HEADER (C/D SIDE) ISOLATION VALVE | 00-4"-DWT6008-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 209 | PD-377
00-VDWT621 | MIXED BED INLET HEADER (A/B SIDE) ISOLATION VALVE | 00-4"-DWT6008-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 210 | PD-377
00-VDWT622 | MIXED BED A INLET ISOLATION VALVE | 00-4"-DWT6011-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 211 | PD-377
00-VDWT623 | MIXED BED D INLET ISOLATION VALVE | 00-4"-DWT6011-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 212 | PD-377
00-VDWT624 | MIXED BED A EFFLUENT ISOLATION VALVE | 00-4"-DWT6168-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 213 | PD-377
00-VDWT625 | MIXED BED B EFFLUENT ISOLATION VALVE | 00-4"-DWT6094-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 214 | PD-377
00-VDWT626 | MIXED BED D EFFLUENT ISOLATION VALVE | 00-4"-DWT6168-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 215 | PD-377
00-VDWT627 | VENT VALVE | 00-0.75"-DWT6013-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | FTE | 110 | 115 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 216 | PD-377
00-VDWT628 | MIXED BED C EFFLUENT ISOLATION VALVE | 00-4"-DWT6093-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 217 | PD-377
00-VDWT629 | INSTRUMENT ISOLATION VALVE | 00-0.75"-DWT6013-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | SWE | 110 | 115 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 218 | PD-377
00-VDWT630 | DEMIN TRAILER EFFLUENT ISOLATION VALVE | 00-3"-DWT6088-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 219 | PD-377
00-VDWT631 | DEMIN TRAILER EFFLUENT ISOLATION VALVE | 00-3"-DWT6092-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 220 | PD-377
00-VDWT632 | DEMIN TRAILER EFFLUENT CHECK VALVE | 00-3"-DWT6092-1BCA2A | 3" | Check valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.2H | INDOOR INSTALLATION PER PIPE ROUTING, SWING-TYPE CHECK VALVE, MAX VELOCITY: 10 FPS. | 221 | PD-377
00-VDWT633 | DEMIN TRAILER EFFLUENT CHECK VALVE | 00-3"-DWT6088-1BCA2A | 3" | Check valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.2H | INDOOR INSTALLATION PER PIPE ROUTING, SWING-TYPE CHECK VALVE, MAX VELOCITY: 10 FPS. | 222 | PD-377
00-VDWT636 | GRAB SAMPLE ISOLATION VALVE | 00-0.5"-DWT6058-1LCR1A | 0.5" | Ball valve | DWT | 1LCR1A | Water | CL600 | CTE | FTE | 110 | 115 | 0.065" Avg. Wall |  | No | 94.03.56.100.5 | INDOOR INSTALLATION PER PIPE ROUTING | 223 | PD-377
00-VDWT637 | INSTRUMENT ISOLATION VALVE | 00-0.75"-DWT6013-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | SWE | 110 | 115 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 224 | PD-377
00-VDWT638 | MIXED BED MANIFOLD EFFLUENT ISOLATION VALVE | 00-4"-DWT6169-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 225 | PD-377
00-VDWT639 | DEMIN SYSTEM EFFLUENT ISOLATION VALVE | 00-4"-DWT6013-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 226 | PD-377
00-VDWT640 | DEMIN DUMP ISOLATION VALVE | 00-4"-DWT6173-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 227 | PD-377
00-VDWT641 | DEMIN TRAILER FEED ISOLATION VALVE | 00-3"-DWT6046-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 228 | PD-376
00-VDWT642 | DEMIN TRAILER FEED ISOLATION VALVE | 00-3"-DWT6047-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 229 | PD-376
00-VDWT643 | WT BUILDING SUMP PUMP A EFFLUENT CHECK VALVE | 00-3"-DWT6031-1BCA2A | 3" | Check valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.2H | INDOOR INSTALLATION PER PIPE ROUTING, SWING-TYPE CHECK VALVE, NORMAL VELOCITY: 8.6 FPS, MAX VELOCITY 19.3 FPS | 230 | PD-378
00-VDWT644 | WT BUILDING SUMP PUMP A EFFLUENT ISOLATION VALVE | 00-3"-DWT6031-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 231 | PD-378
00-VDWT645 | WT BUILDING SUMP PUMP B EFFLUENT CHECK VALVE | 00-3"-DWT6032-1BCA2A | 3" | Check valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.2H | INDOOR INSTALLATION PER PIPE ROUTING, SWING-TYPE CHECK VALVE, NORMAL VELOCITY: 8.6 FPS, MAX VELOCITY 19.3 FPS | 232 | PD-378
00-VDWT646 | WT BUILDING SUMP PUMP B EFFLUENT ISOLATION VALVE | 00-3"-DWT6032-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 233 | PD-378
00-VDWT647 | VENT VALVE | 00-0.75"-DWT6032-1BCA2A | 0.75" | Globe valve | DWT | 1BCA2A | Water | CL800 | SWE | FTE | 110 | 115 | S-40S |  | No | 94.03.68.150.06.2H | INDOOR INSTALLATION PER PIPE ROUTING | 234 | PD-378
00-VDWT651 | DWT INLET FROM SWS ISOLATION VALVE | 00-4"-DWT6015-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 235 | PD-392
00-VDWT656 | RO A INLET ISOLATION VALVE | 00-3"-DWT6018-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 236 | PD-376
00-VDWT658 | RO B INLET ISOLATION | 00-3"-DWT6025-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 237 | PD-376
00-VDWT662 | RO B PERMEATE ISOLATION | 00-3"-DWT6028-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 238 | PD-376
00-VDWT663 | RO A PERMEATE ISOLATION | 00-3"-DWT6030-1BCA2A | 3" | Ball valve | DWT | 1BCA2A | Water | CL150 | RFFE | RFFE | 110 | 115 | S-10S |  | No | 94.03.68.150.03.1 | INDOOR INSTALLATION PER PIPE ROUTING | 239 | PD-376
00-VDWT665 | RO INLET ISOLATION FROM SWS | 00-4"-DWT6015-1BCA2A | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING | 240 | PD-376
00-VDWT666 | INSTRUMENT ISOLATION VALVE | 00-0.5"-DWT6011-1LCR1A | 0.5" | Globe valve | DWT | 1LCR1A | Water | CL600 | CTE | CTE | 110 | 115 | 0.065" Avg. Wall |  | No | 94.03.68.150.06.1 | INDOOR INSTALLATION PER PIPE ROUTING | 241 | PD-377
00-VDWT674 | DEMIN STORAGE TANK ISOLATION VALVE | 00-4"-DWT6171-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S | 1.0 " | Yes | 94.03.68.150.04.1 | OUTDOOR INSTALLATION PER PIPE ROUTING | 242 | PD-410
00-VFGS101 | INSTRUMENT ROOT VALVE | 00-0.75"-FGS6151-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 827 | 230 | S-80 | 1.0 " | No | 94.03.68.150.07.1 |  | 243 | PD-654
00-VFGS102 | INSTRUMENT ROOT VALVE | 00-0.75"-FGS6151-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 827 | 230 | S-80 | 1.0 " | No | 94.03.68.150.07.1 |  | 244 | PD-654
00-VFGS133 | GT FUEL GAS CALORIE METER SAMPLE TUBING ISOLATION | 00-0.375"-FGS1009-1LCR1A | 0.375" | Ball valve | FGS | 1LCR1A | Natural Gas | CL600 | CTE | CTE | 1400 | 230 | 0.065" Avg. Wall |  | No | 94.03.56.100.0 | FIRE SAFE | 245 | PD-654
00-VFGS136 | GT FUEL GAS CALORIE METER SAMPLE TUBING ISOLATION | 00-0.375"-FGS1005-1LCR1A | 0.375" | Ball valve | FGS | 1LCR1A | Natural Gas | CL600 | CTE | CTE | 1400 | 230 | 0.065" Avg. Wall |  | No | 94.03.56.100.0 | FIRE SAFE | 246 | PD-654
00-VFGS137 | GT FUEL GAS CALORIE METER SAMPLE TUBING ISOLATION | 00-0.375"-FGS1009-1LCR1A | 0.375" | Ball valve | FGS | 1LCR1A | Natural Gas | CL600 | CTE | CTE | 1400 | 230 | 0.065" Avg. Wall |  | No | 94.03.56.100.0 | FIRE SAFE | 247 | PD-654
00-VFGS144 | VENT/DRAIN | 00-0.75"-FGS6304-1BAA2A-1.0 "MOC | 0.75" | Gate valve | FGS | 1BAA2A | Oil | CL800 | SWE | SWE | 150 | 160 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 248 | PD-652
00-VFGS145 | DRAIN | 00-0.75"-FGS6302-1BAA2A-1.0 "MOC | 0.75" | Gate valve | FGS | 1BAA2A | Oil | CL800 | SWE | SWE | 150 | 160 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 249 | PD-652
00-VFGS146 | VENT/DRAIN | 00-0.75"-FGS6204-1BAA2A-1.0 "MOC | 0.75" | Gate valve | FGS | 1BAA2A | Oil | CL800 | SWE | SWE | 150 | 160 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 250 | PD-652
00-VFGS147 | DRAIN | 00-0.75"-FGS6202-1BAA2A-1.0 "MOC | 0.75" | Gate valve | FGS | 1BAA2A | Oil | CL800 | SWE | SWE | 150 | 160 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 251 | PD-652
00-VFGS148 | DRAIN | 00-0.75"-FGS6104-1BAA2A-1.0 "MOC | 0.75" | Gate valve | FGS | 1BAA2A | Oil | CL800 | SWE | SWE | 150 | 160 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 252 | PD-652
00-VFGS149 | DRAIN | 00-0.75"-FGS6102-1BAA2A-1.0 "MOC | 0.75" | Gate valve | FGS | 1BAA2A | Oil | CL800 | SWE | SWE | 150 | 160 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 253 | PD-652
00-VFGS150 | VENT | 00-0.75"-FGS6004-1BAA2A-1.0 "MOC | 0.75" | Globe valve | FGS | 1BAA2A | WATER/GLYCOL | CL800 | SWE | SWE | 60 | 210 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 254 | PD-650
00-VFGS151 | VENT | 00-0.75"-FGS6006-1BAA2A-1.0 "MOC | 0.75" | Globe valve | FGS | 1BAA2A | WATER/GLYCOL | CL800 | SWE | SWE | 60 | 210 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 255 | PD-650
00-VFGS152 | VENT | 00-0.75"-FGS6001-1BAA2A-1.0 "MOC | 0.75" | Globe valve | FGS | 1BAA2A | WATER/GLYCOL | CL800 | SWE | SWE | 60 | 210 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 256 | PD-650
00-VFGS200 | EQUIPMENT ISOLATION | 00-16"-FGS6012-1EAL2A-1.0 "MOC | 16" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 827 | 230 | S-60 | 1.0 " | No | 94.03.68.150.07.0 |  | 257 | PD-650
00-VFGS201 | EQUIPMENT ISOLATION | 00-6"-FGS6017-1EAL2A-1.0 "MOC | 6" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 258 | PD-650
00-VFGS208 | COMPRESSOR BYPASS CHECK VALVE | 00-16"-FGS6012-1EAL2A-1.0 "MOC | 16" | Check valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 827 | 230 | S-60 | 1.0 " | No | 94.03.68.150.03.3H | DUAL DISC TYPE (W/ VERTICAL SHAFT), CRACKING PRESSURE < 1 PSID IN HORIZONTAL FLOW ORIENTATION | 259 | PD-650
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 260 | P&ID
00-VFGS209 | COMPRESSOR BYPASS CHECK VALVE | 00-16"-FGS6013-1EAL2A-1.0 "MOC | 16" | Check valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 827 | 230 | S-60 | 1.0 " | No | 94.03.68.150.03.3H | DUAL DISC TYPE (W/ VERTICAL SHAFT), CRACKING PRESSURE < 1 PSID IN HORIZONTAL FLOW ORIENTATION | 261 | PD-650
00-VFGS210 | EQUIPMENT ISOLATION | 00-16"-FGS6013-1EAL2A-1.0 "MOC | 16" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 827 | 230 | S-60 | 1.0 " | No | 94.03.68.150.07.0 |  | 262 | PD-650
00-VFGS220 | FILTER/SEPARATOR INLET | 00-18"-FGS6040-1EAL2A | 18" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 1400 | 130 | S-80 |  | No | 94.03.68.150.07.0 |  | 263 | PD-650
00-VFGS221 | N2 PURGE ISOLATION | 00-0.75"-FGS6040-1EAL2A | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 |  | No | 94.03.68.150.07.0 |  | 264 | PD-650
00-VFGS222 | N2 PURGE ISOLATION | 00-0.75"-FGS6030-1EAL2A | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 |  | No | 94.03.68.150.07.0 |  | 265 | PD-650
00-VFGS224 | EQUIPMENT ISOLATION | 00-4"-FGS6011-1BAA2A-1.0 "MOC | 4" | Butterfly valve | FGS | 1BAA2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 60 | 210 | S-40 | 1.0 " | No | 94.03.68.150.04.0 |  | 266 | PD-650
00-VFGS225 | EQUIPMENT ISOLATION | 00-4"-FGS6006-1BAA2A-1.0 "MOC | 4" | Butterfly valve | FGS | 1BAA2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 60 | 210 | S-40 | 1.0 " | No | 94.03.68.150.04.0 |  | 267 | PD-650
00-VFGS226 | EQUIPMENT ISOLATION | 00-4"-FGS6008-1BAA2A-1.0 "MOC | 4" | Butterfly valve | FGS | 1BAA2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 60 | 210 | S-40 | 1.0 " | No | 94.03.68.150.04.0 |  | 268 | PD-650
00-VFGS227 | AUX BOILER SUPPLY ISOLATION | 00-2"-FGS6224-1EAL2A-1.0 "MOC | 2" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 269 | PD-654
00-VFGS228 | EQUIPMENT ISOLATION | 00-6"-FGS6221-1BAA2A-2.0 "AS | 6" | Ball valve | FGS | 1BAA2A | Natural Gas | CL150 | RFFE | RFFE | 75 | 130 | S-40 | 2.0 " | No | 94.03.68.150.07.0 |  | 270 | PD-654
00-VFGS229 | EQUIPMENT ISOLATION | 00-2"-FGS6024-1EAL2A | 2" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 |  | No | 94.03.68.150.07.0 |  | 271 | PD-650
00-VFGS230 | EMERGENCY SHUT OFF VALVE | 00-18"-FGS6030-1EAL2A | 18" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 1400 | 130 | S-80 |  | No | 94.03.68.150.07.0 |  | 272 | PD-650
00-VFGS238 | EQUIPMENT ISOLATION | 00-4"-FGS6003-1BAA2A-1.0 "MOC | 4" | Butterfly valve | FGS | 1BAA2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 60 | 210 | S-40 | 1.0 " | No | 94.03.68.150.04.0 |  | 273 | PD-650
00-VFGS239 | EQUIPMENT ISOLATION | 00-4"-FGS6001-1BAA2A-1.0 "MOC | 4" | Butterfly valve | FGS | 1BAA2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 60 | 210 | S-40 | 1.0 " | No | 94.03.68.150.04.0 |  | 274 | PD-650
00-VFGS240 | EQUIPMENT ISOLATION | 00-4"-FGS6011-1BAA2A-1.0 "MOC | 4" | Butterfly valve | FGS | 1BAA2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 60 | 210 | S-40 | 1.0 " | No | 94.03.68.150.04.0 |  | 275 | PD-650
00-VFGS241 | STEAM TURBINE BLDG 2 SUPPLY ISOLATION | 00-0.75"-FGS6243-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 276 | PD-654
00-VFGS244 | EQUIPMENT ISOLATION | 00-0.75"-FGS6343-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 277 | PD-654
00-VFGS245 | EQUIPMENT ISOLATION | 00-4"-FGS6004-1BAA2A-1.0 "MOC | 4" | Butterfly valve | FGS | 1BAA2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 60 | 210 | S-40 | 1.0 " | No | 94.03.68.150.04.0 |  | 278 | PD-650
00-VFGS246 | EQUIPMENT ISOLATION | 00-4"-FGS6001-1BAA2A-1.0 "MOC | 4" | Butterfly valve | FGS | 1BAA2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 60 | 210 | S-40 | 1.0 " | No | 94.03.68.150.04.0 |  | 279 | PD-650
00-VFGS253 | EQUIPMENT ISOLATION | 00-18"-FGS6014-1EAL2A-1.0 "MOC | 18" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 827 | 130 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 280 | PD-650
00-VFGS254 | N2 PURGE ISOLATION | 00-0.75"-FGS6106-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 281 | PD-650
00-VFGS257 | EQUIPMENT ISOLATION | 00-18"-FGS6015-1EAL2A-1.0 "MOC | 18" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 827 | 130 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 282 | PD-650
00-VFGS258 | N2 PURGE ISOLATION | 00-0.75"-FGS6206-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 283 | PD-650
00-VFGS259 | EQUIPMENT ISOLATION | 00-6"-FGS6005-1EAL2A-1.0 "MOC | 6" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 284 | PD-650
00-VFGS260 | EQUIPMENT ISOLATION | 00-6"-FGS6016-1EAL2A-1.0 "MOC | 6" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 285 | PD-650
00-VFGS261 | N2 PURGE ISOLATION | 00-0.75"-FGS6016-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 286 | PD-650
00-VFGS262 | N2 PURGE ISOLATION | 00-0.75"-FGS6018-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 287 | PD-650
00-VFGS263 | EQUIPMENT ISOLATION | 00-6"-FGS6018-1EAL2A-1.0 "MOC | 6" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 288 | PD-650
00-VFGS264 | BUILDING SUPPLY HEADER ISOLATION | 00-0.75"-FGS6264-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 289 | PD-654
00-VFGS265 | EQUIPMENT ISOLATION | 00-1"-FGS6265-1BAA2A-1.0 "AS | 1" | Ball valve | FGS | 1BAA2A | Natural Gas | CL600 | SWE | SWE | 75 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 290 | PD-654
00-VFGS272 | EQUIPMENT ISOLATION | 00-3"-FGS6144-1BAA2A-1.5 "AS | 3" | Ball valve | FGS | 1BAA2A | Natural Gas | CL150 | RFFE | RFFE | 75 | 130 | S-40 | 1.5 " | No | 94.03.68.150.07.0 |  | 291 | PD-654
00-VFGS273 | EQUIPMENT ISOLATION | 00-3"-FGS6244-1BAA2A-1.5 "AS | 3" | Ball valve | FGS | 1BAA2A | Natural Gas | CL150 | RFFE | RFFE | 75 | 130 | S-40 | 1.5 " | No | 94.03.68.150.07.0 |  | 292 | PD-654
00-VFGS278 | EQUIPMENT ISOLATION | 00-0.375"-FGS6022-1LCR1A | 0.375" | Ball valve | FGS | 1LCR1A | Natural Gas | CL600 | CTE | CTE | 1400 | 230 | 0.065" Avg. Wall |  | No | 94.03.56.100.0 | FIRE SAFE | 293 | PD-651
00-VFGS279 | EQUIPMENT ISOLATION | 00-0.375"-FGS6019-1LCR1A | 0.375" | Ball valve | FGS | 1LCR1A | Natural Gas | CL600 | CTE | CTE | 1400 | 230 | 0.065" Avg. Wall |  | No | 94.03.56.100.0 | FIRE SAFE | 294 | PD-651
00-VFGS280 | EQUIPMENT ISOLATION | 00-0.375"-FGS6021-1LCR1A | 0.375" | Ball valve | FGS | 1LCR1A | Natural Gas | CL600 | CTE | CTE | 1400 | 230 | 0.065" Avg. Wall |  | No | 94.03.56.100.0 | FIRE SAFE | 295 | PD-651
00-VFGS281 | N2 PURGE ISOLATION | 00-0.75"-FGS6115-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 827 | 230 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 296 | PD-652
00-VFGS282 | N2 PURGE ISOLATION | 00-0.75"-FGS6215-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 827 | 230 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 297 | PD-652
00-VFGS283 | N2 PURGE ISOLATION | 00-0.75"-FGS6315-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 827 | 230 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 298 | PD-652
00-VFGS300 | N2 PURGE ISOLATION | 00-0.75"-FGS6010-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 299 | PD-654
00-VFGS301 | N2 PURGE ISOLATION | 00-0.75"-FGS6151-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 827 | 230 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 300 | PD-654
00-VFGS302 | FG NITROGEN SUPPLY ISOLATION | 00-1"-FGS6044-1BAA2A | 1" | Ball valve | FGS | 1BAA2A | Nitrogen | CL600 | SWE | SWE | 145 | 140 | S-80 |  | No | 94.03.68.150.06.0 |  | 301 | PD-652
00-VFGS303 | FG NITROGEN SUPPLY ISOLATION | 00-1"-FGS6045-1BAA2A | 1" | Ball valve | FGS | 1BAA2A | Nitrogen | CL600 | SWE | SWE | 145 | 140 | S-80 |  | No | 94.03.68.150.06.0 |  | 302 | PD-652
00-VFGS304 | FG NITROGEN SUPPLY ISOLATION | 00-1"-FGS6046-1BAA2A | 1" | Ball valve | FGS | 1BAA2A | Nitrogen | CL600 | SWE | SWE | 145 | 140 | S-80 |  | No | 94.03.68.150.06.0 |  | 303 | PD-652
00-VFGS309 | N2 PURGE ISOLATION | 00-0.75"-FGS6224-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 304 | PD-654
00-VFGS310 | BUILDING SUPPLY HEADER ISOLATION | 00-0.75"-FGS6264-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 305 | PD-654
00-VFGS311 | N2 PURGE ISOLATION | 00-0.75"-FGS6265-1BAA2A-1.0 "AS | 0.75" | Ball valve | FGS | 1BAA2A | Natural Gas | CL600 | SWE | SWE | 75 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 306 | PD-654
00-VFGS312 | N2 PURGE ISOLATION | 00-0.75"-FGS6221-1BAA2A-1.0 "AS | 0.75" | Ball valve | FGS | 1BAA2A | Natural Gas | CL600 | SWE | SWE | 75 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 307 | PD-654
00-VFGS313 | STEAM TURBINE BLDG 1 SUPPLY ISOLATION | 00-0.75"-FGS6343-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 308 | PD-654
00-VFGS314 | N2 PURGE ISOLATION | 00-0.75"-FGS6144-1BAA2A-1.0 "AS | 0.75" | Ball valve | FGS | 1BAA2A | Natural Gas | CL600 | SWE | SWE | 75 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 309 | PD-654
00-VFGS315 | STEAM TURBINE BLDG 2 SUPPLY ISOLATION | 00-0.75"-FGS6243-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 310 | PD-654
00-VFGS316 | N2 PURGE ISOLATION | 00-0.75"-FGS6244-1BAA2A-1.0 "AS | 0.75" | Ball valve | FGS | 1BAA2A | Natural Gas | CL600 | SWE | SWE | 75 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 311 | PD-654
00-VFPS601 | UNIT 1 NORTHEAST HYDRANT ISOLATION | 00-8"-FPS0603-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 312 | PD-471
00-VFPS604 | UNIT 1 EAST HYDRANT ISOLATION | 00-8"-FPS0606-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 313 | PD-471
00-VFPS612 | UNIT 1 ACC NORTHWEST HYDRANT ISOLATION | 00-8"-FPS0613-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 314 | PD-471
00-VFPS615 | AUX BOILER NORTH HYDRANT ISOLATION | 00-8"-FPS0620-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 315 | PD-471
00-VFPS622 | UNIT 1 ACC NORTHEAST HYDRANT ISOLATION | 00-8"-FPS0618-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 316 | PD-471
00-VFPS625 | UNIT 2 NORTHEAST HYDRANT ISOLATION | 00-8"-FPS0630-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 317 | PD-471
00-VFPS635 | FIRE WATER/SERVICE WATER TANK ISOLATION | 00-12"-FPS6035-FBAH2A-1.0 "MOH | 12" | Gate valve | FPS | FBAH2A | Water | CL125 | FFFE | FFFE | 179 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.03.0 | FLEXIBLE WEDGE - PROVIDE TAMPER SWITCH | 318 | PD-390
00-VFPS640 | PARKING AREA HYDRANT ISOLATION | 00-8"-FPS0635-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 319 | PD-471
00-VFPS642 | UNIT 1 NORTH HYDRANT ISOLATION | 00-8"-FPS0628-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 320 | PD-471
00-VFPS648 | UNIT 2 ACC SOUTHWEST HYDRANT ISOLATION | 00-8"-FPS0643-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 321 | PD-471
00-VFPS652 | UNIT 2 EAST HYDRANT ISOLATION | 00-8"-FPS0638-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 322 | PD-471
00-VFPS656 | FIRE WATER/SERVICE WATER TANK ISOLATION | 00-14"-FPS6049-FBAH2A-1.0 "MOH | 14" | Butterfly valve | FPS | FBAH2A | Water | CL125 | LUGGED | LUGGED | 179 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 323 | PD-390
00-VFPS670 | UNIT 2 SOUTHEAST HYDRANT ISOLATION | 00-8"-FPS0665-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 324 | PD-471
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 325 | P&ID
00-VFPS672 | UNIT 1 ACC SOUTHWEST HYDRANT ISOLATION | 00-8"-FPS0658-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 326 | PD-471
00-VFPS675 | UNIT 2 ACC SOUTHEAST HYDRANT ISOLATION | 00-8"-FPS0687-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 327 | PD-471
00-VFPS680 | FIRE WATER/SERVICE WATER TANK ISOLATION | 00-12"-FPS6080-FBAH2A-1.0 "MOH | 12" | Gate valve | FPS | FBAH2A | Water | CL125 | FFFE | FFFE | 179 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.03.0 | FLEXIBLE WEDGE - PROVIDE TAMPER SWITCH | 328 | PD-390
00-VFPS682 | UNIT 1 WEST HYDRANT ISOLATION | 00-8"-FPS0632-FPEA1U | 8" | Gate valve | FPS | FPEA1U | Water | CL250 | FFFE | FFFE | 179 | 110 | CL350 |  | No | 93.70.02 |  | 329 | PD-471
00-VINA128 | DRAIN | 00-0.75"-INA6310-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 330 | PD-558
00-VINA189 | END USER ISOLATION | 00-0.75"-INA6237-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 331 | PD-558
00-VINA201 | END USER ISOLATION | 00-0.75"-INA6007-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 332 | PD-561
00-VINA273 | END USER ISOLATION | 00-0.75"-INA6142-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 333 | PD-556
00-VINA274 | END USER ISOLATION | 00-0.75"-INA6143-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 334 | PD-556
00-VINA330 | END USER ISOLATION | 00-0.75"-INA6310-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 335 | PD-558
00-VINA333 | END USER ISOLATION | 00-0.75"-INA6259-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 336 | PD-554
00-VINA339 | END USER ISOLATION | 00-0.75"-INA6257-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 337 | PD-558
00-VINA341 | END USER ISOLATION | 00-0.75"-INA6256-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 338 | PD-558
00-VINA342 | END USER ISOLATION | 00-0.75"-INA6281-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 339 | PD-558
00-VINA353 | END USER ISOLATION | 00-0.75"-INA6255-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 340 | PD-558
00-VINA390 | UNIT 2 PULSE AIR RECEIVER ISOLATION | 00-2.5"-INA6522-1BCD2A | 2.5" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 341 | PD-561
00-VINA391 | UNIT 2 PULSE AIR RECEIVER ISOLATION | 00-2.5"-INA6525-1BCD2A | 2.5" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 342 | PD-561
00-VINA392 | DRAIN | 00-0.75"-INA6522-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 343 | PD-561
00-VINA393 | DRAIN | 00-0.75"-INA6525-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 344 | PD-561
00-VINA394 | UNIT 2 PULSE AIR RECEIVER BYPASS | 00-2.5"-INA6526-1BCD2A | 2.5" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 345 | PD-561
00-VINA395 | INSTRUMENT | 00-0.75"-INA6518-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 346 | PD-560
00-VINA396 | UNIT 2 PULSE AIR RECEIVER DRAIN ISOLATION | 00-0.75"-INA6532-1LCR3A | 0.75" | Ball valve | INA | 1LCR3A | AIR | CL300 | CTE | CTE | 145 | 140 | 0.065" Avg. Wall |  | No | 94.03.68.150.06.0 |  | 347 | PD-561
00-VINA397 | UNIT 2 PULSE AIR RECEIVER AUTOMATED DRAIN BYPASS | 00-0.75"-INA6533-1LCR3A | 0.75" | Ball valve | INA | 1LCR3A | AIR | CL300 | CTE | CTE | 145 | 140 | 0.065" Avg. Wall |  | No | 94.03.68.150.06.0 |  | 348 | PD-561
00-VINA403 | UNIT 1 PULSE AIR RECEIVER BYPASS | 00-2.5"-INA6511-1BCD2A | 2.5" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 349 | PD-560
00-VINA404 | UNIT 1 PULSE AIR RECEIVER ISOLATION | 00-2.5"-INA6509-1BCD2A | 2.5" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 350 | PD-560
00-VINA405 | UNIT 1 PULSE AIR RECEIVER ISOLATION | 00-2.5"-INA6513-1BCD2A | 2.5" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 351 | PD-560
00-VINA406 | DRAIN | 00-0.75"-INA6513-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 352 | PD-560
00-VINA407 | DRAIN | 00-0.75"-INA6509-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 353 | PD-560
00-VINA408 | UNIT 1 PULSE AIR RECEIVER DRAIN ISOLATION | 00-0.75"-INA6507-1LCR3A | 0.75" | Ball valve | INA | 1LCR3A | AIR | CL300 | CTE | CTE | 145 | 140 | 0.065" Avg. Wall |  | No | 94.03.68.150.06.0 |  | 354 | PD-560
00-VINA409 | UNIT 1 PULSE AIR RECEIVER AUTOMATED DRAIN BYPASS | 00-0.75"-INA6515-1LCR3A | 0.75" | Ball valve | INA | 1LCR3A | AIR | CL300 | CTE | CTE | 145 | 140 | 0.065" Avg. Wall |  | No | 94.03.68.150.06.0 |  | 355 | PD-560
00-VINA410 | INSTRUMENT | 00-0.75"-INA6530-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 356 | PD-561
00-VINA601 | STUB-UP ISOLATION | 00-0.75"-INA6001-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 357 | PD-562
00-VINA603 | STUB-UP ISOLATION | 00-1"-INA6003-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 358 | PD-562
00-VINA604 | DRAIN | 00-0.75"-INA6138-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 359 | PD-556
00-VINA605 | END USER ISOLATION | 00-0.75"-INA6024-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 360 | PD-553
00-VINA606 | END USER ISOLATION | 00-0.75"-INA6016-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 361 | PD-553
00-VINA609 | END USER ISOLATION | 00-0.75"-INA6009-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 362 | PD-556
00-VINA611 | END USER ISOLATION | 00-1"-INA7056-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 363 | PD-556
00-VINA613 | END USER ISOLATION | 00-0.75"-INA6013-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 364 | PD-556
00-VINA614 | STUB-UP ISOLATION | 00-2"-INA6067-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 365 | PD-557
00-VINA615 | DRAIN | 00-0.75"-INA6148-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 366 | PD-550
00-VINA616 | END USER ISOLATION | 00-0.75"-INA6073-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 367 | PD-557
00-VINA617 | END USER ISOLATION | 00-0.75"-INA6017-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 368 | PD-556
00-VINA618 | DRAIN | 00-0.75"-INA6026-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 369 | PD-556
00-VINA619 | DRAIN | 00-0.75"-INA6030-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 370 | PD-556
00-VINA620 | STUB-UP ISOLATION | 00-0.75"-INA6097-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 371 | PD-557
00-VINA621 | END USER ISOLATION | 00-0.75"-INA6021-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 372 | PD-556
00-VINA623 | END USER ISOLATION | 00-0.75"-INA6023-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 373 | PD-556
00-VINA625 | END USER ISOLATION | 00-0.75"-INA6025-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 374 | PD-556
00-VINA627 | END USER ISOLATION | 00-0.75"-INA6027-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 375 | PD-556
00-VINA629 | STUB-UP ISOLATION | 00-1"-INA6029-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 376 | PD-554
00-VINA631 | WET AIR RECEIVER AUTOMATED DRAIN BYPASS | 00-0.75"-INA6131-1LCR3A-1.0 "MOH | 0.75" | Ball valve | INA | 1LCR3A | AIR | CL300 | CTE | CTE | 145 | 140 | 0.065" Avg. Wall | 1.0 " | Yes | 94.03.68.150.06.0 |  | 377 | PD-550
00-VINA632 | END USER ISOLATION | 00-0.75"-INA6032-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 378 | PD-556
00-VINA633 | END USER ISOLATION | 00-0.75"-INA6033-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 379 | PD-554
00-VINA635 | END USER ISOLATION | 00-0.75"-INA6035-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 380 | PD-554
00-VINA636 | AIR COMPRESSOR 01A ISOLATION | 00-4"-INA6160-1BCD2A-1.0 "MOH | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S | 1.0 " | Yes | 94.03.68.150.03.2 |  | 381 | PD-550
00-VINA637 | END USER ISOLATION | 00-0.75"-INA6037-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 382 | PD-553
00-VINA639 | END USER ISOLATION | 00-0.75"-INA6039-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 383 | PD-553
00-VINA643 | END USER ISOLATION | 00-0.75"-INA6043-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 384 | PD-553
00-VINA644 | TEMPORARY AIR COMPRESSOR CONNECTION ISOLATION | 00-4"-INA6146-1BCD2A-1.0 "MOH | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S | 1.0 " | Yes | 94.03.68.150.03.2 |  | 385 | PD-550
00-VINA645 | END USER ISOLATION | 00-0.75"-INA7011-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 386 | PD-555
00-VINA647 | END USER ISOLATION | 00-0.75"-INA6047-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 387 | PD-555
00-VINA648 | AIR COMPRESSOR 01B ISOLATION | 00-4"-INA6148-1BCD2A-1.0 "MOH | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S | 1.0 " | Yes | 94.03.68.150.03.2 |  | 388 | PD-550
00-VINA649 | DRY AIR RECEIVER DRAIN ISOLATION | 00-0.75"-INA6149-1LCR3A | 0.75" | Ball valve | INA | 1LCR3A | AIR | CL300 | CTE | CTE | 145 | 140 | 0.065" Avg. Wall |  | No | 94.03.68.150.06.0 |  | 389 | PD-551
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 390 | P&ID
00-VINA651 | END USER ISOLATION | 00-0.75"-INA6051-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 391 | PD-555
00-VINA652 | DRAIN | 00-0.75"-INA6143-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 392 | PD-556
00-VINA653 | END USER ISOLATION | 00-0.75"-INA6053-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 393 | PD-555
00-VINA655 | STUB-UP ISOLATION | 00-2"-INA6055-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL600 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 394 | PD-554
00-VINA657 | END USER ISOLATION | 00-0.75"-INA6057-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 395 | PD-554
00-VINA659 | END USER ISOLATION | 00-0.75"-INA6059-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 396 | PD-554
00-VINA660 | WET AIR RECEIVER ISOLATION | 00-4"-INA6160-1BCD2A-1.0 "MOH | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S | 1.0 " | Yes | 94.03.68.150.03.2 |  | 397 | PD-550
00-VINA661 | END USER ISOLATION | 00-0.75"-INA6061-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 398 | PD-554
00-VINA662 | WET AIR RECEIVER BYPASS | 00-4"-INA6162-1BCD2A-1.0 "MOH | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S | 1.0 " | Yes | 94.03.68.150.03.2 |  | 399 | PD-550
00-VINA663 | STUB-UP ISOLATION | 00-0.75"-INA6063-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 400 | PD-554
00-VINA664 | WET AIR RECEIVER DRAIN ISOLATION | 00-0.75"-INA6144-1LCR3A-1.0 "MOH | 0.75" | Ball valve | INA | 1LCR3A | AIR | CL300 | CTE | CTE | 145 | 140 | 0.065" Avg. Wall | 1.0 " | Yes | 94.03.68.150.06.0 |  | 401 | PD-550
00-VINA665 | END USER ISOLATION | 00-0.75"-INA6065-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 402 | PD-557
00-VINA666 | INSTRUMENT | 00-0.75"-INA6188-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 403 | PD-551
00-VINA668 | DRY AIR RECEIVER ISOLATION | 00-4"-INA6000-1BCD2A | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 404 | PD-551
00-VINA669 | STUB-UP ISOLATION | 00-0.75"-INA6069-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 405 | PD-557
00-VINA670 | DRAIN | 00-0.75"-INA6160-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 406 | PD-550
00-VINA671 | END USER ISOLATION | 00-0.75"-INA6071-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 407 | PD-557
00-VINA672 | INSTRUMENT | 00-0.75"-INA6172-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 408 | PD-550
00-VINA673 | DRAIN | 00-0.75"-INA6019-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 409 | PD-556
00-VINA674 | WET AIR RECEIVER ISOLATION | 00-4"-INA6052-1BCD2A-1.0 "MOH | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S | 1.0 " | Yes | 94.03.68.150.03.2 |  | 410 | PD-550
00-VINA675 | DRAIN | 00-0.75"-INA6178-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 411 | PD-551
00-VINA676 | DRAIN | 00-0.75"-INA6174-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 412 | PD-551
00-VINA677 | END USER ISOLATION | 00-0.75"-INA6077-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 413 | PD-557
00-VINA678 | DRY AIR RECEIVER ISOLATION | 00-4"-INA6178-1BCD2A | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 414 | PD-551
00-VINA680 | INSTRUMENT | 00-0.75"-INA6000-1BCD2A | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S |  | No | 94.03.68.150.06.0 |  | 415 | PD-551
00-VINA681 | END USER ISOLATION | 00-0.75"-INA6081-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 416 | PD-557
00-VINA682 | DRY AIR RECEIVER AUTOMATED DRAIN BYPASS | 00-0.75"-INA6181-1LCR3A | 0.75" | Ball valve | INA | 1LCR3A | AIR | CL300 | CTE | CTE | 145 | 140 | 0.065" Avg. Wall |  | No | 94.03.68.150.06.0 |  | 417 | PD-551
00-VINA683 | END USER ISOLATION | 00-0.75"-INA6083-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 418 | PD-552
00-VINA684 | END USER ISOLATION | 00-0.75"-INA6084-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 419 | PD-552
00-VINA685 | STUB-UP ISOLATION | 00-0.75"-INA6085-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 420 | PD-552
00-VINA686 | DRAIN | 00-0.75"-INA6004-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 421 | PD-550
00-VINA687 | STUB-UP ISOLATION | 00-0.75"-INA6087-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 422 | PD-552
00-VINA688 | DRAIN | 00-0.75"-INA6014-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 423 | PD-550
00-VINA689 | STUB-UP ISOLATION | 00-0.75"-INA6089-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 424 | PD-552
00-VINA690 | DRAIN | 00-0.75"-INA6052-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 425 | PD-550
00-VINA691 | STUB-UP ISOLATION | 00-1"-INA6091-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 426 | PD-552
00-VINA692 | DRAIN | 00-0.75"-INA6160-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 427 | PD-550
00-VINA693 | DRAIN | 00-0.75"-INA6174-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 428 | PD-550
00-VINA694 | DRAIN | 00-0.75"-INA6000-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 429 | PD-551
00-VINA695 | END USER ISOLATION | 00-0.75"-INA6095-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 430 | PD-553
00-VINA696 | DRY AIR RECEIVER BYPASS | 00-4"-INA6177-1BCD2A | 4" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 431 | PD-551
00-VINA697 | END USER ISOLATION | 00-0.75"-INA6097-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 432 | PD-557
00-VINA698 | STUB-UP ISOLATION | 00-0.75"-INA6099-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 433 | PD-557
00-VINA699 | END USER ISOLATION | 00-0.75"-INA6079-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 434 | PD-557
00-VINA702 | END USER ISOLATION | 00-0.75"-INA6102-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 435 | PD-553
00-VINA703 | END USER ISOLATION | 00-0.75"-INA6103-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 436 | PD-553
00-VINA704 | END USER ISOLATION | 00-0.75"-INA6104-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 437 | PD-553
00-VINA706 | STUB-UP ISOLATION | 00-1"-INA6138-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 438 | PD-556
00-VINA716 | DRAIN | 00-0.75"-INA6119-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 439 | PD-551
00-VINA718 | DRAIN | 00-0.75"-INA6104-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 440 | PD-553
00-VINA719 | DRAIN | 00-0.75"-INA7017-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 441 | PD-553
00-VINA720 | END USER ISOLATION | 00-0.75"-INA7065-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 442 | PD-554
00-VINA721 | END USER ISOLATION | 00-0.75"-INA7062-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 443 | PD-554
00-VINA722 | STUB-UP ISOLATION | 00-1"-INA6040-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 444 | PD-554
00-VINA723 | END USER ISOLATION | 00-1"-INA7055-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 445 | PD-554
00-VINA725 | END USER ISOLATION | 00-1"-INA6285-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 446 | PD-554
00-VINA726 | STUB-UP ISOLATION | 00-1"-INA6041-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 447 | PD-554
00-VINA728 | END USER ISOLATION | 00-0.75"-INA6257-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 448 | PD-558
00-VINA729 | DRAIN | 00-0.75"-INA7067-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 449 | PD-553
00-VINA730 | STUB-UP ISOLATION | 00-1"-INA6066-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 450 | PD-554
00-VINA731 | STUB-UP ISOLATION | 00-1"-INA6020-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 451 | PD-553
00-VINA732 | STUB-UP ISOLATION | 00-1"-INA7001-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 452 | PD-553
00-VINA733 | STUB-UP ISOLATION | 00-1"-INA7002-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 453 | PD-553
00-VINA734 | DRAIN | 00-0.75"-INA7058-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 454 | PD-553
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 455 | P&ID
00-VINA735 | END USER ISOLATION | 00-1"-INA6072-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 456 | PD-553
00-VINA736 | END USER ISOLATION | 00-1"-INA6074-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 457 | PD-553
00-VINA737 | END USER ISOLATION | 00-1"-INA6093-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 458 | PD-553
00-VINA738 | STUB-UP ISOLATION | 00-0.75"-INA7068-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 459 | PD-553
00-VINA739 | END USER ISOLATION | 00-1"-INA7017-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 460 | PD-553
00-VINA740 | STUB-UP ISOLATION | 00-1"-INA7021-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 461 | PD-553
00-VINA741 | END USER ISOLATION | 00-1"-INA7020-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 462 | PD-553
00-VINA742 | END USER ISOLATION | 00-1"-INA7067-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 463 | PD-553
00-VINA743 | END USER ISOLATION | 00-1"-INA7058-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 464 | PD-553
00-VINA744 | DRAIN | 00-0.75"-INA7021-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 465 | PD-553
00-VINA747 | STUB-UP ISOLATION | 00-2.5"-INA6522-1BCD2A | 2.5" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 466 | PD-554
00-VINA749 | DRAIN | 00-0.75"-INA6066-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 467 | PD-554
00-VINA766 | STUB-UP ISOLATION | 00-0.75"-INA6007-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 468 | PD-562
00-VINA767 | DRAIN | 00-0.75"-INA6028-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 469 | PD-558
00-VINA772 | DRAIN | 00-0.75"-INA7020-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 470 | PD-553
00-VINA792 | STUB-UP ISOLATION | 00-2.5"-INA6509-1BCD2A | 2.5" | Ball valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-10S |  | No | 94.03.68.150.03.2 |  | 471 | PD-557
00-VINA805 | STUB-UP ISOLATION | 00-1"-INA6026-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 472 | PD-556
00-VINA806 | STUB-UP ISOLATION | 00-1"-INA6030-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 473 | PD-556
00-VINA807 | STUB-UP ISOLATION | 00-0.75"-INA6032-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 474 | PD-556
00-VINA808 | STUB-UP ISOLATION | 00-1"-INA6048-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 475 | PD-556
00-VINA809 | STUB-UP ISOLATION | 00-1"-INA6060-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 476 | PD-556
00-VINA810 | END USER ISOLATION | 00-1"-INA6075-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 477 | PD-556
00-VINA811 | STUB-UP ISOLATION | 00-1"-INA6019-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 478 | PD-556
00-VINA812 | DRAIN | 00-0.75"-INA6147-1BCD2A-1.0 "MOH | 0.75" | Ball valve | INA | 1BCD2A | AIR | CL600 | SWE | SWE | 145 | 140 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 479 | PD-550
00-VINA816 | END USER ISOLATION | 00-0.75"-INA6011-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 480 | PD-556
00-VINA817 | END USER ISOLATION | 00-1"-INA6145-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 481 | PD-556
00-VINA820 | END USER ISOLATION | 00-1"-INA7057-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 482 | PD-556
00-VINA824 | END USER ISOLATION | 00-1"-INA6577-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 483 | PD-554
00-VPDR600 | AMMONIA CONTAINMENT ISOLATION | 00-4"-PDR0631-1WGJ2U | 4" | Gate valve | PDR | 1WGJ2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | SDR 11 |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 484 | PD-974
00-VPDR601 | FUEL GAS CONTAINMENT ISOLATION | 00-4"-PDR0644-1WGJ2U | 4" | Gate valve | PDR | 1WGJ2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | SDR 11 |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 485 | PD-974
00-VPDR602 | WATER TREATMENT TRENCH ISOLATION | 00-4"-PDR0672-1WGJ2U | 4" | Gate valve | PDR | 1WGJ2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | SDR 11 |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 486 | PD-974
00-VPDR603 | TRANSFORMER CONTAINMENT ISOLATION | 00-4"-PDR0669-1ADA2U | 4" | Gate valve | PDR | 1ADA2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 487 | PD-974
00-VPDR604 | SUMP PUMP CHECK VALVE | 00-2"-PDR6003-1BAB2A-1.0 "MOH | 2" | Check valve | PDR | 1BAB2A | Water | CL800 | SWE | SWE | 50 | 125 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | PISTON | 488 | PD-975
00-VPDR605 | SUMP PUMP ISOLATION | 00-2"-PDR6003-1BAB2A-1.0 "MOH | 2" | Ball valve | PDR | 1BAB2A | Water | CL600 | SWE | SWE | 50 | 125 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 489 | PD-975
00-VPDR606 | SUMP PUMP CHECK VALVE | 00-2"-PDR6002-1BAB2A-1.0 "MOH | 2" | Check valve | PDR | 1BAB2A | Water | CL800 | SWE | SWE | 50 | 125 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | PISTON | 490 | PD-975
00-VPDR607 | SUMP PUMP ISOLATION | 00-2"-PDR6002-1BAB2A-1.0 "MOH | 2" | Ball valve | PDR | 1BAB2A | Water | CL600 | SWE | SWE | 50 | 125 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 491 | PD-975
00-VPDR608 | SUMP PUMP CHECK VALVE | 00-2"-PDR6004-1BAB2A-1.0 "MOH | 2" | Check valve | PDR | 1BAB2A | Water | CL800 | SWE | SWE | 50 | 125 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | PISTON | 492 | PD-975
00-VPDR609 | SUMP PUMP ISOLATION | 00-2"-PDR6004-1BAB2A-1.0 "MOH | 2" | Ball valve | PDR | 1BAB2A | Water | CL600 | SWE | SWE | 50 | 125 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 493 | PD-975
00-VPDR610 | SUMP PUMP CHECK VALVE | 00-2"-PDR6005-1BAB2A-1.0 "MOH | 2" | Check valve | PDR | 1BAB2A | Water | CL800 | SWE | SWE | 50 | 125 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | PISTON | 494 | PD-975
00-VPDR611 | SUMP PUMP ISOLATION | 00-2"-PDR6005-1BAB2A-1.0 "MOH | 2" | Ball valve | PDR | 1BAB2A | Water | CL600 | SWE | SWE | 50 | 125 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 495 | PD-975
00-VPWS061 | ISOLATE CONSTRUCTION | 00-3"-PWS0605-1BGC0U | 3" | Gate Valve with Handwheel | PWS | 1BGC0U | Water | CL200 | FFFE | FFFE | 80 | 115 | SDR 11 |  | No | 93.70.02 |  | 496 | PD-400
00-VPWS063 | ISOLATE PERMANENT TIE-IN | 00-12"-PWS0601-1BGC0U | 12" | Gate Valve with Handwheel | PWS | 1BGC0U | Water | CL200 | FFFE | FFFE | 80 | 115 | SDR 11 |  | No | 93.70.02 |  | 497 | PD-400
00-VPWS601 | VENT | 00-0.75"-PWS6004-1BCA0A | 0.75" | Ball valve | PWS | 1BCA0A | Water | CL600 | SWE | SWE | 80 | 115 | S-40S |  | No | 94.03.68.150.06.0 | VALVE IS TO BE NSF 61 CERTIFIED | 498 | PD-400
00-VPWS605 | ADMIN BUILDING ISOLATION | 00-2"-PWS6004-1BCA0A | 2" | Ball valve | PWS | 1BCA0A | Water | CL600 | SWE | SWE | 80 | 115 | S-40S |  | No | 94.03.68.150.06.0 | VALVE IS TO BE NSF 61 CERTIFIED | 499 | PD-400
00-VPWS611 | ISOLATION VALVE FOR EWS 611 | 00-1.25"-PWS6111-1BCA3A-1.0 "MIC | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | No | 94.03.68.150.06.0 |  | 500 | PD-402
00-VPWS612 | ISOLATION VALVE FOR EWS 612 | 00-1.25"-PWS6112-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 501 | PD-402
00-VPWS613 | ISOLATION VALVE FOR EWS 613 | 00-1.25"-PWS6113-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 502 | PD-402
00-VPWS614 | ISOLATION VALVE FOR EWS 614 | 00-1.25"-PWS6114-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 503 | PD-402
00-VPWS615 | ISOLATION VALVE FOR EWS 615 | 00-1.25"-PWS6115-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 504 | PD-402
00-VPWS616 | ISOLATION VALVE FOR EWS 616 | 00-1.25"-PWS6116-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 505 | PD-402
00-VPWS617 | ISOLATION VALVE FOR EWS 617 | 00-1.25"-PWS6117-1BCA3A-1.0 "MIC | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | No | 94.03.68.150.06.0 |  | 506 | PD-402
00-VPWS618 | ISOLATION VALVE FOR EWS 618 | 00-1.25"-PWS6118-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 507 | PD-402
00-VPWS619 | ISOLATION VALVE FOR EWS 619 | 00-1.25"-PWS6119-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 508 | PD-402
00-VPWS620 | ISOLATION VALVE FOR EWS 620 | 00-1.25"-PWS6120-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 509 | PD-402
00-VPWS621 | ISOLATION VALVE FOR EWS 621 | 00-1.25"-PWS6121-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 510 | PD-402
00-VPWS622 | ISOLATION VALVE FOR EWE 622 | 00-1"-PWS6122-1BCA3A-1.0 "MIC | 1" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | No | 94.03.68.150.06.0 |  | 511 | PD-402
00-VPWS623 | ISOLATION VALVE FOR EWS 623 | 00-1.25"-PWS6123-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 512 | PD-402
00-VPWS624 | ISOLATION VALVE FOR EWS 624 & 628 | 00-1.25"-PWS6124-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 513 | PD-402
00-VPWS625 | ISOLATION VALVE FOR EWE 625 | 00-1"-PWS6125-1BCA3A-1.0 "MIC | 1" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | No | 94.03.68.150.06.0 |  | 514 | PD-402
00-VPWS626 | ISOLATION VALVE FOR EWS 626 | 00-1.25"-PWS6126-1BCA3A-1.0 "MOH | 1.25" | Ball valve | PWS | 1BCA3A | Water | CL600 | SWE | SWE | 140 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 515 | PD-402
00-VSDR600 | FORCE MAIN ISOLATION FROM TEMPORARY LIFT STATION | 00-3"-SDR0624-1BGC2U | 3" | Gate valve | SDR | 1BGC2U | Water | CL150 | FFFE | FFFE | 50 | 125 | SDR 11 |  | No | 93.70.02 |  | 516 | PD-950
00-VSDR601 | TEMPORARY LIFT STATION BRANCH ISOLATION | 00-3"-SDR0625-1BGC2U | 3" | Gate valve | SDR | 1BGC2U | Water | CL150 | FFFE | FFFE | 50 | 125 | SDR 11 |  | No | 93.70.02 |  | 517 | PD-950
00-VSMP108 | AUX STEAM SAMPLE LINE DRAIN VALVE | 00-0.5"-SMP6469-1LCR1A | 0.5" | Ball valve | SMP | 1LCR1A | Steam/Water | CL600 | CTE | CTE | 425 | 470 | 0.065" Avg. Wall |  | No | 94.03.56.100.0 |  | 518 | PD-501
00-VSMP109 | AUX STEAM SAMPLE LINE DRAIN VALVE | 00-0.5"-SMP6469-1LCR1A | 0.5" | Ball valve | SMP | 1LCR1A | Steam/Water | CL600 | CTE | CTE | 425 | 470 | 0.065" Avg. Wall |  | No | 94.03.56.100.0 |  | 519 | PD-501
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 520 | P&ID
00-VSWS554 | INSTRUMENTATION | 00-0.5"-SWS6031-1BAB3A | 0.5" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 521 | PD-121
00-VSWS556 | INSTRUMENTATION | 00-0.5"-SWS6031-1BAB3A | 0.5" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 522 | PD-121
00-VSWS601 | UTS ISOLATION | 00-1"-SWS6001-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 523 | PD-392
00-VSWS602 | SWS TANK ISOLATION | 00-3"-SWS6002-1BAH1A-1.0 "MOH | 3" | Gate valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.03.0 |  | 524 | PD-390
00-VSWS603 | UTS ISOLATION | 00-1"-SWS6003-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 525 | PD-392
00-VSWS604 | INSTRUMENTATION | 00-2"-SWS6019-1BAB3A-1.0 "MOH | 2" | Ball valve | SWS | 1BAB3A | Water | CL150 | RFFE | RFFE | 50 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 526 | PD-390
00-VSWS605 | SWS TANK ISOLATION - PUMP RECIRC | 00-6"-SWS6076-1BAH1A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 527 | PD-390
00-VSWS606 | INSTRUMENTATION | 00-2"-SWS6020-1BAB3A-1.0 "MOH | 2" | Ball valve | SWS | 1BAB3A | Water | CL150 | RFFE | RFFE | 50 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 528 | PD-390
00-VSWS607 | UTS ISOLATION | 00-1"-SWS6007-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 529 | PD-392
00-VSWS608 | INSTRUMENTATION | 00-0.75"-SWS6168-1BAB3A-1.0 "MOH | 0.75" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 530 | PD-391
00-VSWS609 | UTS ISOLATION | 00-1"-SWS6009-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 531 | PD-392
00-VSWS610 | SWS TANK DRAIN | 00-6"-SWS6010-1BAB3A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAB3A | Water | CL150 | LUGGED | LUGGED | 50 | 110 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 532 | PD-390
00-VSWS611 | UTS ISOLATION | 00-1"-SWS6011-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 533 | PD-392
00-VSWS612 | SWS TANK ISOLATION | 00-10"-SWS6012-1BAH1A-1.0 "MOH | 10" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 534 | PD-390
00-VSWS613 | UTS ISOLATION | 00-1"-SWS6013-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 535 | PD-392
00-VSWS614 | UTS ISOLATION | 00-1"-SWS6016-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 536 | PD-392
00-VSWS615 | SWS TANK ISOLATION | 00-12"-SWS6014-1BAH1A-1.0 "MOH | 12" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 537 | PD-390
00-VSWS616 | BEARING FLUSH ISOLATION | 00-1"-SWS6041-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 538 | PD-393
00-VSWS617 | UTS ISOLATION | 00-1"-SWS6017-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 539 | PD-392
00-VSWS618 | SWS TANK ISOLATION - PUMP SUCTION | 00-10"-SWS6018-1BAH1A-1.0 "MOH | 10" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 540 | PD-390
00-VSWS619 | DRAIN | 00-0.75"-SWS6030-1BAB3A-1.0 "MOH | 0.75" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 541 | PD-961
00-VSWS620 | VENT | 00-0.75"-SWS6030-1BAB3A-1.0 "MOH | 0.75" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 542 | PD-961
00-VSWS621 | UTS ISOLATION | 00-1"-SWS6021-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 543 | PD-392
00-VSWS622 | POTABLE WATER MAKEUP CV BYPASS | 00-4"-SWS6075-1BAH1A-1.0 "MOH | 4" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 80 | 115 | S-STD | 1.0 " | Yes | 94.03.68.150.04.2 |  | 544 | PD-390
00-VSWS623 | UTS ISOLATION | 00-1"-SWS6023-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 545 | PD-392
00-VSWS624 | POTABLE WATER MAKEUP CV ISOLATION | 00-6"-SWS6074-1BAH1A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 80 | 115 | S-STD | 1.0 " | Yes | 94.03.68.150.04.2 |  | 546 | PD-390
00-VSWS625 | UTS ISOLATION | 00-1"-SWS6025-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 547 | PD-392
00-VSWS626 | VENT | 00-0.75"-SWS6031-1BAB3A | 0.75" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.2H |  | 548 | PD-121
00-VSWS627 | UTS ISOLATION | 00-1"-SWS6027-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 549 | PD-392
00-VSWS629 | UTS ISOLATION | 00-1"-SWS6029-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 550 | PD-393
00-VSWS630 | SERVICE WATER TO WASTEWATER SUMP | 00-4"-SWS6030-1BAH1A-1.0 "MOH | 4" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 551 | PD-961
00-VSWS633 | UTS ISOLATION | 00-1"-SWS6033-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 552 | PD-393
00-VSWS635 | UTS ISOLATION | 00-1"-SWS6035-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 553 | PD-393
00-VSWS637 | UTS ISOLATION | 00-1"-SWS6037-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 554 | PD-394
00-VSWS639 | UTS ISOLATION | 00-1"-SWS6039-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 555 | PD-393
00-VSWS649 | UTS ISOLATION | 00-1"-SWS6047-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 556 | PD-393
00-VSWS651 | UTS ISOLATION | 00-1"-SWS6051-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 557 | PD-393
00-VSWS653 | UTS ISOLATION | 00-1"-SWS6053-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 558 | PD-393
00-VSWS654 | UTS ISOLATION | 00-1"-SWS6083-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 559 | PD-394
00-VSWS655 | UTS ISOLATION | 00-1"-SWS6055-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 560 | PD-393
00-VSWS657 | UTS ISOLATION | 00-1"-SWS6057-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 561 | PD-393
00-VSWS659 | UTS ISOLATION | 00-1"-SWS6059-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 562 | PD-393
00-VSWS661 | UTS ISOLATION | 00-1"-SWS6061-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 563 | PD-393
00-VSWS663 | UTS ISOLATION | 00-1"-SWS6063-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 564 | PD-393
00-VSWS665 | UTS ISOLATION | 00-1"-SWS6065-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 565 | PD-394
00-VSWS667 | UTS ISOLATION | 00-1"-SWS6067-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 566 | PD-394
00-VSWS668 | INSTRUMENTATION | 00-0.75"-SWS6068-1BAB3A-1.0 "MOH | 0.75" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 567 | PD-391
00-VSWS669 | UTS ISOLATION | 00-1"-SWS6069-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 568 | PD-394
00-VSWS671 | UTS ISOLATION | 00-1"-SWS6071-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 569 | PD-394
00-VSWS672 | RECIRC CV ISOLATION | 00-6"-SWS6076-1BAH1A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 570 | PD-391
00-VSWS673 | UTS ISOLATION | 00-1"-SWS6073-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 571 | PD-394
00-VSWS676 | RECIRC CV ISOLATION | 00-6"-SWS6076-1BAH1A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 572 | PD-391
00-VSWS677 | UTS ISOLATION | 00-1"-SWS6043-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 573 | PD-394
00-VSWS679 | UTS ISOLATION | 00-1"-SWS6079-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 574 | PD-395
00-VSWS680 | RECIRC CV BYPASS | 00-4"-SWS6080-1BAH1A-1.0 "MOH | 4" | Globe valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.03.2H | THROTTLING SERVICE | 575 | PD-391
00-VSWS681 | UTS ISOLATION | 00-1"-SWS6081-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 576 | PD-394
00-VSWS682 | VENT | 00-0.75"-SWS6076-1BAB3A-1.0 "MOH | 0.75" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 577 | PD-391
00-VSWS683 | UTS ISOLATION | 00-1"-SWS6045-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 578 | PD-393
00-VSWS684 | UTS ISOLATION | 00-1"-SWS6084-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 579 | PD-394
00-VSWS685 | UTS ISOLATION | 00-1"-SWS6085-1BAB3A | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 |  | No | 94.03.68.150.06.0 |  | 580 | PD-394
00-VSWS686 | DRAIN | 00-0.75"-SWS6076-1BAB3A-1.0 "MOH | 0.75" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 581 | PD-391
00-VSWS687 | UTS ISOLATION | 00-1"-SWS6087-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 582 | PD-394
00-VSWS689 | UTS ISOLATION | 00-1"-SWS6089-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 583 | PD-394
00-VSWS690 | SWS TANK ISOLATION | 00-8"-SWS6004-1BAH1A-1.0 "MOH | 8" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 584 | PD-390
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 585 | P&ID
00-VSWS691 | UTS ISOLATION | 00-1"-SWS6091-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 586 | PD-394
00-VSWS692 | DRAIN | 00-0.75"-SWS6074-1BAB3A-1.0 "MOH | 0.75" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 80 | 115 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 587 | PD-390
00-VSWS694 | POTABLE WATER MAKEUP CV ISOLATION | 00-6"-SWS6074-1BAH1A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 80 | 115 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 588 | PD-390
00-VSWS695 | UTS ISOLATION | 00-1"-SWS6095-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 589 | PD-394
00-VSWS696 | SWS TANK ISOLATION - POTABLE MAKEUP | 00-6"-SWS6074-1BAH1A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 80 | 115 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 590 | PD-390
00-VSWS697 | UTS ISOLATION | 00-1"-SWS6097-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 591 | PD-394
00-VSWS698 | UTS ISOLATION | 00-1"-SWS6077-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 592 | PD-395
00-VSWS699 | UTS ISOLATION | 00-1"-SWS6099-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 593 | PD-394
00-VWDR601 | INSTRUMENT ISOLATION | 00-0.75"-WDR6373-1BAB2A-1.0 "MOH | 0.75" | Ball valve | WDR | 1BAB2A | Water | CL600 | SWE | SWE | 70 | 140 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 594 | PD-961
00-VWDR602 | INSTRUMENT ISOLATION | 00-0.5"-WDR6000-1BAB2A-1.0 "MOH | 0.5" | Ball valve | WDR | 1BAB2A | Water | CL800 | SWE | SWE | 70 | 140 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 595 | PD-961
00-VWDR603 | INSTRUMENT ISOLATION | 00-0.5"-WDR6001-1BAB2A-1.0 "MOH | 0.5" | Ball valve | WDR | 1BAB2A | Water | CL800 | SWE | SWE | 70 | 140 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 596 | PD-961
00-VWDR604 | FREE CHLORINE SAMPLE ISOLATION | 00-1"-WDR6002-1BAB2A-1.0 "MOH | 1" | Ball valve | WDR | 1BAB2A | Water | CL600 | SWE | SWE | 70 | 140 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 597 | PD-961
00-VWDR605 | FREE CHLORINE SAMPLE RETURN ISOLATION | 00-1"-WDR6003-1BAB2A-1.0 "MOH | 1" | Ball valve | WDR | 1BAB2A | Water | CL600 | SWE | SWE | 70 | 140 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 598 | PD-961
00-VWDR633 | WASTEWATER SUMP PUMP B CHECK VALVE | 00-10"-WDR6335-1BAB2A-1.0 "MOH | 10" | Check valve | WDR | 1BAB2A | Water | CL150 | WAFER | WAFER | 70 | 140 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | DUAL PLATE; MAX FLOW - 2500 GPM, MIN FLOW - 250 GPM | 599 | PD-961
00-VWDR635 | WASTEWATER SUMP PUMP B ISOLATION | 00-10"-WDR6335-1BAB2A-1.0 "MOH | 10" | Butterfly valve | WDR | 1BAB2A | Water | CL150 | LUGGED | LUGGED | 70 | 140 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 600 | PD-961
00-VWDR673 | WASTEWATER SUMP PUMP A CHECK VALVE | 00-10"-WDR6373-1BAB2A-1.0 "MOH | 10" | Check valve | WDR | 1BAB2A | Water | CL150 | WAFER | WAFER | 70 | 140 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | DUAL PLATE; MAX FLOW - 2500 GPM, MIN FLOW - 250 GPM | 601 | PD-961
00-VWDR674 | WASTEWATER SUMP PUMP A ISOLATION | 00-10"-WDR6373-1BAB2A-1.0 "MOH | 10" | Butterfly valve | WDR | 1BAB2A | Water | CL150 | LUGGED | LUGGED | 70 | 140 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 602 | PD-961
00-YV-BDN301 | BLOWDOWN DISCHARGE CONTROL VALVE TO SWS TANK | 00-8"-BDN6113-1BAA2A-1.0 "MOH | 8" | Globe control valve | BDN | 1BAA2A | Water | CL150 | RFFE | RFFE | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 603 | PD-091
00-YV-BDN321 | BLOWDOWN DISCHARGE CONTROL VALVE TO WDR SUMP | 00-6"-BDN6687-1BAA2A-1.0 "MOH | 6" | Globe control valve | BDN | 1BAA2A | Water | CL150 | RFFE | RFFE | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 604 | PD-091
00-YV-DWT115 | DEMIN SYSTEM EFFLUENT ON/OFF VALVE | 00-4"-DWT6013-1BCA2A | 4" | Butterfly control valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.100.02.4 | VALVES TO BE SUPPLIED WITH LIMIT SWITCHES, INDOOR INSTALLATION PER PIPE ROUTING | 605 | PD-377
00-YV-DWT125 | DEMIN DUMP DIVERT VALVE | 00-4"-DWT6173-1BCA2A | 4" | Butterfly control valve | DWT | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 110 | 115 | S-10S |  | No | 94.03.68.100.02.4 | VALVES TO BE SUPPLIED WITH LIMIT SWITCHES, INDOOR INSTALLATION PER PIPE ROUTING | 606 | PD-377
01-FCV-BFW147 | BFP A MIN RECIRC CV | 01-3"-BFW1066-1HBB1A-1.0 "EOH | 3" | Angle globe control valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.100.02.0 |  | 607 | PD-061A
01-FCV-BFW187 | BFP B MIN RECIRC CV | 01-3"-BFW1074-1HBB1A-1.0 "EOH | 3" | Angle globe control valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.100.02.0 |  | 608 | PD-061A
01-FCV-BFW343 | CT TCA COOLER BFW TCV TO HRSG | 01-4"-BFW1324-1HBB1A-2.0 "EOH | 4" | Angle globe control valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.0 " | Yes | 94.03.68.100.02.0 |  | 609 | PD-063A
01-FCV-BFW359 | CT TCA COOLER BFW TCV RECIRC TO ACC | 01-3"-BFW1426-1HBB1A-2.0 "EOH | 3" | Angle globe control valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.0 " | Yes | 94.03.68.100.02.0 |  | 610 | PD-063A
01-FCV-BFW459 | FG HX BFW FCV TO LP ECON | 01-2"-BFW1008-1FAC1A-1.0 "EOH | 2" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.100.02.0 |  | 611 | PD-064A
01-FCV-BFW475 | FG HX BFW FCV RECIRC TO ACC | 01-2"-BFW1093-1FBB1A-EOH | 2" | Globe control valve | BFW | 1FBB1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 |  | Yes | 94.03.68.100.02.0 |  | 612 | PD-064A
01-FCV-CND331 | CONDENSATE MINIMUM RECIRC VALVE | 01-6"-CND1161-1EAA2A-1.0 "MOH | 6" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.100.02.0 |  | 613 | PD-053A
01-LCV-DWS715 | CONDENSER MAKEUP LEVEL CONTROL | 01-2"-DWS1017-1BCA2A-1.0 "MOH | 2" | Globe control valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.3 |  | 614 | PD-050A
01-LV-CRH109 | DRIP LEG DRAIN - AUTOMATED | 01-2"-CRH1025-1EBB1A-3.5 "EIC | 2" | Ball control valve | CRH | 1EBB1A | Steam | CL600 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 615 | PD-030A
01-LV-CRH110 | DRIP LEG DRAIN - AUTOMATED | 01-2"-CRH1026-1EBA1A-2.0 "EOH | 2" | Ball control valve | CRH | 1EBA1A | Steam | CL600 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 616 | PD-030A
01-LV-CRH125 | DRIP LEG DRAIN - AUTOMATED | 01-2"-CRH1004-1EBA1A-2.0 "EOH | 2" | Ball control valve | CRH | 1EBA1A | Steam | CL600 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 617 | PD-031A
01-LV-LPS115 | DRIP LEG DRAIN - AUTOMATED | 01-2"-LPS1401-1DAA1A-2.0 "EIC | 2" | Ball control valve | LPS | 1DAA1A | Steam | CL600 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 618 | PD-040A
01-LV-LPS123 | DRIP LEG DRAIN - AUTOMATED | 01-2"-LPS1429-1DAA1A-2.0 "EIC | 2" | Ball control valve | LPS | 1DAA1A | Steam | CL600 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 619 | PD-041A
01-MOV-AXS321 | UNIT 1 ISOLATION | 01-6"-AXS1500-1DAA1A-1.5 "EOC | 6" | Control valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.150.03.0 | MOTOR OPERATOR, FLEXIBLE WEDGE, 3-WAY DRAIN W/ LOW PRESSURE SIDE MOTOR OPERATED VALVE, LIMIT SWITCHES | 620 | PD-123A
01-MOV-BFW139 | BFP A IP DISCHARGE ISOLATION MOV | 01-6"-BFW1374-1FAC1A-1.5 "EOH | 6" | Control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0 | PARALLEL SLIDE DISC, 3-WAY DRAIN WITH LOW PRESSURE SIDE MOTOR OPERATED VALVE | 621 | PD-060A
01-MOV-BFW145 | BFP A HP DISCHARGE ISOLATION MOV | 01-10"-BFW1029-1HAC2A-1.5 "EOH | 10" | Control valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0 | PARALLEL SLIDE DISC, 3-WAY DRAIN WITH LOW PRESSURE SIDE MOTOR OPERATED VALVE | 622 | PD-061A
01-MOV-BFW179 | BFP B IP DISCHARGE ISOLATION MOV | 01-6"-BFW1063-1FAC1A-1.5 "EOH | 6" | Control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0 | PARALLEL SLIDE DISC, 3-WAY DRAIN WITH LOW PRESSURE SIDE MOTOR OPERATED VALVE | 623 | PD-060A
01-MOV-BFW185 | BFP B HP DISCHARGE ISOLATION MOV | 01-10"-BFW1052-1HAC2A-1.5 "EOH | 10" | Control valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0 | PARALLEL SLIDE DISC, 3-WAY DRAIN WITH LOW PRESSURE SIDE MOTOR OPERATED VALVE | 624 | PD-061A
01-MOV-CND201 | CONDENSATE IRON FILTER AUTOMATIC ISOLATION | 01-12"-CND1037-1EAA2A-1.0 "MOH | 12" | Control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1 | PARALLEL SLIDE DISC, MOTOR OPERATOR | 625 | PD-052A
01-MOV-CND211 | CONDENSATE IRON FILTER AUTOMATIC ISOLATION | 01-12"-CND1027-1EAA2A-1.0 "MOH | 12" | Control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1 | PARALLEL SLIDE DISC, MOTOR OPERATOR | 626 | PD-052A
01-MOV-CND221 | CONDENSATE IRON FILTER AUTOMATIC BYPASS | 01-12"-CND1088-1EAA2A-1.0 "MOH | 12" | Control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1 | FLEXIBLE WEDGE, MOTOR OPERATOR | 627 | PD-052A
01-PCV-AXS713 | DA EJECTOR STEAM SUPPLY CONTROL VALVE | 01-1"-AXS1508-1DAA1A-1.0 "EOC | 1" | Globe control valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.100.02.1 | HYDRO VALVE KIT | 628 | PD-050A
01-PCV-CCW191 | SYSTEM BALANCING CONTROL VALVE | 01-10"-CCW1141-1BAB2A | 10" | Ball control valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.100.02.3 |  | 629 | PD-270A
01-PCV-CMG117 | CO2 BACKPRESSURE REGULATOR | 01-2"-CMG1010-1BCB6A | 2" | Self contained backpress reg | CMG | 1BCB6A | CARBON DIOXIDE | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.100.02.2 |  | 630 | PD-571
01-PCV-CND289 | ACC DUCT CURTAIN SPRAY CONTROL VALVE | 01-2.5"-CND1038-1EAA2A-1.0 "MIC | 2.5" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.100.02.1 |  | 631 | PD-052A
01-PCV-CND423 | CND LP ECON AND DRUM BYPASS CONTROL VALVE | 01-6"-CND1020-1EAA2A-1.0 "MOH | 6" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.100.02.0 |  | 632 | PD-053A
01-PCV-CND455 | LP ECONOMIZER INLET PCV | 01-8"-CND1187-1EAA2A-1.0 "MOH | 8" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 633 | PD-053A
01-PCV-CRH700 | CRH TO AXS PRESSURE LETDOWN (LOW FLOW) | 01-2"-CRH1193-1EBA1A-2.5 "EOC | 2" | Globe control valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-80 | 2.5 " | No | 94.03.68.100.01.2 | - | 634 | PD-124A
01-PCV-CRH715 | CRH TO AXS PRESSURE LETDOWN (HIGH FLOW) | 01-6"-CRH1162-1EBA1A-3.0 "EOC | 6" | Globe control valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 3.0 " | No | 94.03.68.100.01.2 | - | 635 | PD-124A
01-PCV-HPS100 | HPS BYPASS VALVE | 01-10"-HPS1175-1HBD2A-6.0 "EOC | 10" | Steam Bypass Valve | HPS | 1HBD2A | Steam | CL2500 SPL | BE | BE | 2534 | 1097 | 1.171" min | 6.0 " | No | 94.03.68.100.01.0 |  | 636 | PD-020A
01-PCV-HRH100 | BYPASS VALVE | 01-24"-HRH1265-1FBD1A-7.0 "EIC | 24" | Angle control valve | HRH | 1FBD1A | Steam | CL600 SPL | BE | BE | 586 | 1096 | S-60 | 7.0 " | No | 94.03.68.100.01.0 | - | 637 | PD-034A
01-PCV-LPS100 | BYPASS VALVE | 01-12"-LPS1463-1DAA1A-3.0 "EIC | 12" | Angle control valve | LPS | 1DAA1A | Steam | CL150 | BE | BE | 119 | 624 | S-STD | 3.0 " | No | 94.03.68.100.01.0 | - | 638 | PD-040A
01-PRV-CMG101 | NITROGEN STORAGE CYLINDER RACK OUTLET | 01-1"-CMG1101-1BCA1A | 1" | Self contained press red reg | CMG | 1BCA1A | NITROGEN | CL600 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.100.02.2 |  | 639 | PD-570
01-PRV-CMG102 | NITROGEN STORAGE CYLINDER RACK OUTLET | 01-1"-CMG1102-1BCA1A | 1" | Self contained press red reg | CMG | 1BCA1A | NITROGEN | CL600 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.100.02.2 |  | 640 | PD-570
01-PRV-CMG115 | CO2 PRESSURE REGULATOR | 01-1.5"-CMG1011-1BCB6A-1.0 "MOH | 1.5" | Self contained backpress reg | CMG | 1BCB6A | CARBON DIOXIDE | CL600 | SWE | SWE | 200 | 115 | S-40S | 1.0 " | Yes | 94.03.68.100.02.3 |  | 641 | PD-571
01-PRV-CND325 | STEAM DRAINS PUMP SEAL WATER PRV | 01-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Self contained press red reg | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.3 |  | 642 | PD-306A
01-PRV-CND326 | STEAM DRAINS PUMP SEAL WATER PRV | 01-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Self contained press red reg | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.3 |  | 643 | PD-306A
01-PRV-CTP112 | EVAP COOLER PRESSURE REGULATOR | 01-3"-CTP1060-1BCA2A-1.0 "MOH | 3" | Self contained press red reg | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 644 | PD-333A
01-PRV-SWS713 | BEARING FLUSH PRESSURE REGULATOR | 01-1"-SWS1031-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 645 | PD-090A
01-PSV-AXS325 | STEAM HEADER SAFETY VALVE | 01-4"-AXS1934-1DAA1A-1.5 "EOC | 4" | Angle press relief valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.175.0 |  | 646 | PD-123A
01-PSV-AXS329 | HEAT EXCHANGER RELIEF VALVE | 01-0.75"-AXS1042-1DAA1A-1.0 "EOC | 0.75" | Angle press relief valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.175.0 |  | 647 | PD-123A
01-PSV-BFW104 | BFP SUCTION HEADER PSV | 01-4"-BFW1096-1DAA1A-1.0 "EOH | 4" | Angle press relief valve | BFW | 1DAA1A | Water | CL300 | RFFE | RFFE | 300 | 360 | S-40 | 1.0 " | Yes | 94.03.68.175.0 |  | 648 | PD-060A
01-PSV-BFW105 | BFP A SUCTION OVERPRESSURE PROTECTION | 01-1.5"-BFW1024-1DAA1A-1.0 "EOH | 1.5" | Angle press relief valve | BFW | 1DAA1A | Water | CL300 | RFFE | RFFE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 649 | PD-060A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 650 | P&ID
01-PSV-BFW155 | BFP B SUCTION OVERPRESSURE PROTECTION | 01-1.5"-BFW1022-1DAA1A-1.0 "EOH | 1.5" | Angle press relief valve | BFW | 1DAA1A | Water | CL300 | RFFE | RFFE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 651 | PD-060A
01-PSV-BFW323 | CT TCA COOLER OVERPRESSURE PROTECTION | 01-1"-BFW1318-1HAC2A-1.0 "EOH | 1" | Angle press relief valve | BFW | 1HAC2A | Water | CL2500 | SWE | RFFE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.175.0 |  | 652 | PD-063A
01-PSV-BFW423 | FG HX OVERPRESSURE PROTECTION | 01-0.75"-BFW1483-1FAC1A-1.0 "EOH | 0.75" | Angle press relief valve | BFW | 1FAC1A | Water | CL900 | SWE | RFFE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 653 | PD-064A
01-PSV-BFW463 | FG STARTUP HEATER PSV | 01-0.75"-BFW1106-1FAC1A-1.0 "EOH | 0.75" | Angle press relief valve | BFW | 1FAC1A | Water | CL900 | SWE | RFFE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 654 | PD-064A
01-PSV-BFW751 | FG HX OUTLET CND RETURN PSV | 01-1.5"-BFW1146-1EAA1A-1.0 "EOH | 1.5" | Angle press relief valve | BFW | 1EAA1A | Water | CL600 | BE | RFFE | 790 | 589 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 655 | PD-053A
01-PSV-CCW213 | RELIEF VALVE | 01-0.75"-CCW1166-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 656 | PD-271A
01-PSV-CCW223 | RELIEF VALVE | 01-0.75"-CCW1104-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 657 | PD-271A
01-PSV-CCW233 | RELIEF VALVE | 01-0.75"-CCW1169-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 658 | PD-271A
01-PSV-CCW243 | RELIEF VALVE | 01-0.75"-CCW1107-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 659 | PD-271A
01-PSV-CCW253 | RELIEF VALVE | 01-0.75"-CCW1181-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 660 | PD-271A
01-PSV-CCW311 | RELIEF VALVE | 01-0.75"-CCW1207-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 661 | PD-272A
01-PSV-CCW331 | RELIEF VALVE | 01-0.75"-CCW1221-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 662 | PD-272A
01-PSV-CCW351 | RELIEF VALVE | 01-0.75"-CCW1241-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 663 | PD-272A
01-PSV-CCW381 | RELIEF VALVE | 01-0.75"-CCW1321-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 664 | PD-273A
01-PSV-CCW391 | RELIEF VALVE | 01-0.75"-CCW1309-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 665 | PD-273A
01-PSV-CCW413 | RELIEF VALVE | 01-0.75"-CCW1089-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 666 | PD-274A
01-PSV-CCW423 | RELIEF VALVE | 01-0.75"-CCW1088-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 667 | PD-274A
01-PSV-CCW433 | RELIEF VALVE | 01-0.75"-CCW1087-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 668 | PD-274A
01-PSV-CCW443 | RELIEF VALVE | 01-0.75"-CCW1086-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 669 | PD-274A
01-PSV-CCW453 | RELIEF VALVE | 01-0.75"-CCW1085-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 670 | PD-274A
01-PSV-CCW463 | RELIEF VALVE | 01-0.75"-CCW1084-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 671 | PD-274A
01-PSV-CCW473 | RELIEF VALVE | 01-0.75"-CCW1083-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 672 | PD-274A
01-PSV-CCW483 | RELIEF VALVE | 01-0.75"-CCW1082-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 673 | PD-274A
01-PSV-CCW511 | RELIEF VALVE | 01-0.75"-CCW1080-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 674 | PD-275A
01-PSV-CCW531 | RELIEF VALVE | 01-0.75"-CCW1090-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 675 | PD-275A
01-PSV-CMG116 | NITROGEN OVERPRESSURE PROTECTION | 01-1"-CMG1116-1BCA1A | 1" | Angle press relief valve | CMG | 1BCA1A | NITROGEN | CL150 | RFFE | RFFE | 130 | 115 | S-40S |  | No | 94.03.68.175.2 |  | 676 | PD-570
01-PSV-CMG118 | CO2 OVERPRESSURE PROTECTION | 01-1"-CMG1018-1BCB6A | 1" | Angle press relief valve | CMG | 1BCB6A | CARBON DIOXIDE | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.175.2 |  | 677 | PD-571
01-PSV-CMG126 | NITROGEN OVERPRESSURE PROTECTION | 01-1"-CMG1126-1BCA1A | 1" | Angle press relief valve | CMG | 1BCA1A | NITROGEN | CL150 | RFFE | RFFE | 130 | 115 | S-40S |  | No | 94.03.68.175.2 |  | 678 | PD-570
01-PSV-CND101 | CND PUMP A SUCTION OVERPRESSURE PROTECTION | 01-0.75"-CND1011-1BAA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1BAA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 679 | PD-051A
01-PSV-CND121 | CND PUMP B SUCTION OVERPRESSURE PROTECTION | 01-0.75"-CND1019-1BAA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1BAA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 680 | PD-051A
01-PSV-CND141 | CND PUMP C SUCTION OVERPRESSURE PROTECTION | 01-0.75"-CND1013-1BAA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1BAA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 681 | PD-051A
01-PSV-CND255 | DEMIN FILL TO CND OVERPERSSURE PROTECTION | 01-0.75"-CND1111-1BCA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1BCA2A | Water | CL150 | SWE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.175.0 |  | 682 | PD-052A
01-PSV-CND402 | CONDENSATE FILL TO HP BFW OVERPRESSURE PROTECTION | 01-0.75"-CND1156-1EAA2A-1.0 "MOH | 0.75" | Angle control valve | CND | 1EAA2A | Water | CL600 | SWE | RFFE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 683 | PD-061A
01-PSV-CND403 | CONDENSATE FILL TO IP BFW OVERPRESSURE PROTECTION | 01-0.75"-CND1003-1EAA2A-1.0 "MOH | 0.75" | Angle control valve | CND | 1EAA2A | Water | CL600 | SWE | RFFE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 684 | PD-062A
01-PSV-CND457 | LP ECONOMIZER INLET OVERPRESSURE PROTECTION | 01-4"-CND1687-1DAA2A-1.0 "MOH | 4" | Angle press relief valve | CND | 1DAA2A | Water | CL300 | RFFE | RFFE | 600 | 290 | S-40 | 1.0 " | Yes | 94.03.68.175.0 |  | 685 | PD-053A
01-PSV-CND519 | ECA COOLER THERMAL RELIEF OVERPRESSURE PROTECTION | 01-1"-CND1221-1EAA1A-1.0 "EOH | 1" | Angle press relief valve | CND | 1EAA1A | Water | CL600 | RFFE | RFFE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 686 | PD-054A
01-PSV-CTP118 | EVAP COOLER OVERPRESSURE PROTECTION | 01-1"-CTP1010-1BCA2A-1.0 "MOH | 1" | Angle control valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.175.1 |  | 687 | PD-333A
01-PSV-CTP128 | CT CASING COOLING AIR PIPING PSV | 01-0.75"-CTP1020-1BCA2A | 0.75" | Angle press relief valve | CTP | 1BCA2A | AIR | CL150 | RFFE | RFFE | 145 | 212 | S-40S |  | No | 94.03.68.175.2 |  | 688 | PD-336A
01-PSV-FGS159 | PERFORMANCE HEATER PSV | 01-1"-FGS1036-1EAL1A-1.0 "EOC | 1" | Angle press relief valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.175.1 |  | 689 | PD-656A
01-PSV-INA100 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1043-1BCD2A | 0.75" | Angle press relief valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-40S |  | No | 94.03.68.175.2 |  | 690 | PD-552
01-PSV-INA101 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1047-1BCD2A | 0.75" | Angle press relief valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-40S |  | No | 94.03.68.175.2 |  | 691 | PD-552
01-PSV-INA104 | OVERPRESSURE PROTECTION | 01-0.75"-INA1084-1BCD2A | 0.75" | Angle press relief valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-40S |  | No | 94.03.68.175.2 |  | 692 | PD-559
01-PSV-INA105 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1106-1BCD2A | 0.75" | Angle press relief valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-40S |  | No | 94.03.68.175.2 |  | 693 | PD-552
01-PSV-STP209 | GLAND STEAM PSV | 01-3"-STP1004-1DAA1A-2.5 "EIC | 3" | Angle press relief valve | STP | 1DAA1A | Steam | CL300 | RFFE | RFFE | 100 | 797 | S-40 | 2.5 " | No | 94.03.68.175.1 |  | 694 | PD-300A
01-TCV-AXS371 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE | 01-1"-AXS1505-1DCA1A-1.0 "EOH | 1" | Globe control valve | AXS | 1DCA1A | Steam/Water | CL300 | RFFE | RFFE | 425 | 470 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 | HYDRO VALVE KIT | 695 | PD-123A
01-TCV-AXS711 | CONDENSATE TANK SPARGING STEAM CONTROL VALVE | 01-3"-AXS1507-1DAA1A-1.5 "EOC | 3" | Globe control valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.100.02.1 | HYDRO VALVE KIT | 696 | PD-050A
01-TCV-BFW716 | HP BYPASS SPRAY SUPPLY TCV | 01-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.100.01.0 |  | 697 | PD-020A
01-TCV-BFW749 | CRH LETDOWN PCV SPRAY TCV | 01-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 698 | PD-124A
01-TCV-BFW761 | CRH LETDOWN ATTEMPERATOR SPRAY TCV | 01-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 699 | PD-124A
01-TCV-CCW181 | ACHE BYPASS CONTROL VALVE | 01-24"-CCW1141-1BAB2A | 24" | Butterfly control valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-20 |  | No | 94.03.68.100.02.3 |  | 700 | PD-270A
01-TCV-CND706 | CRH VENTILATOR DSH SPRAY TCV | 01-2"-CND1062-1EAA2A-1.0 "MIC | 2" | Globe control valve | CND | 1EAA2A | Water | CL600 | RFFE | RFFE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.100.01.3 |  | 701 | PD-030A
01-TCV-CND707 | HRH BYPASS SPRAY TCV | 01-4"-CND1256-1EAA2A-1.0 "MIC | 4" | Globe control valve | CND | 1EAA2A | Water | CL600 | RFFE | RFFE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.100.01.0 |  | 702 | PD-034A
01-TCV-CND717 | HP DRAINS TANK QUENCH SPRAY TCV | 01-1.5"-CND1202-1EAA2A-1.0 "MOH | 1.5" | Globe control valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 703 | PD-304A
01-TCV-CND718 | LP DRAINS TANK QUENCH SPRAY TCV | 01-2"-CND1200-1EAA2A-1.0 "MOH | 2" | Globe control valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 704 | PD-305A
01-TCV-CND726 | LP BYPASS SPRAY TCV | 01-1"-CND1459-1EAA2A-1.0 "MIC | 1" | Globe control valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.100.01.0 |  | 705 | PD-040A
01-TV-HPS123 | DRIP LEG DRAIN - AUTOMATED | 01-2"-HPS1015-1HBD2A-4.0 "EIC | 2" | Ball control valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 4.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 706 | PD-021A
01-TV-HRH117 | DRIP LEG DRAIN - AUTOMATED | 01-2"-HRH1112-1FBD1A-4.0 "EIC | 2" | Ball control valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 707 | PD-034A
01-TV-SWS717 | BLOWDOWN QUENCH CONTROL VALVE | 01-2"-SWS1016-1BAH1A-1.0 "MOH | 2" | Globe control valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 708 | PD-090A
01-VAQA101 | UNIT 1 AFCU ISOLATION VALVE | 01-1"-AQA1001-1BCD2A | 1" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 709 | PD-782
01-VAXS101 | VENT | 01-0.75"-AXS1510-1DAA1A-1.5 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 710 | PD-123A
01-VAXS102 | INSTRUMENT | 01-0.75"-AXS1072-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 711 | PD-050A
01-VAXS103 | TRAP ISOLATION | 01-0.75"-AXS1015-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 712 | PD-122A
01-VAXS104 | TRAP ISOLATION | 01-0.75"-AXS1004-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 713 | PD-123A
01-VAXS105 | TRAP ISOLATION | 01-0.75"-AXS1004-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 714 | PD-123A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 715 | P&ID
01-VAXS106 | DRAIN | 01-0.75"-AXS1004-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 716 | PD-123A
01-VAXS107 | TRAP BYPASS | 01-0.75"-AXS1151-1DAA1A-2.0 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 717 | PD-123A
01-VAXS108 | VENT | 01-0.75"-AXS1499-1DAA1A-1.5 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.3H |  | 718 | PD-120
01-VAXS109 | INSTRUMENT | 01-2"-AXS1005-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 719 | PD-123A
01-VAXS110 | INSTRUMENT | 01-2"-AXS1019-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 720 | PD-123A
01-VAXS112 | TRAP ISOLATION | 01-0.75"-AXS1018-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 721 | PD-122A
01-VAXS113 | TRAP DRAIN | 01-2"-AXS1253-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 722 | PD-122A
01-VAXS115 | TRAP ISOLATION | 01-0.75"-AXS1018-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 723 | PD-122A
01-VAXS116 | DRAIN | 01-0.75"-AXS1018-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 724 | PD-122A
01-VAXS117 | TRAP ISOLATION | 01-0.75"-AXS1132-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 725 | PD-123A
01-VAXS118 | TRAP ISOLATION | 01-0.75"-AXS1024-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 726 | PD-123A
01-VAXS119 | DRAIN | 01-0.75"-AXS1132-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 727 | PD-123A
01-VAXS120 | TRAP BYPASS | 01-0.75"-AXS1148-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 728 | PD-123A
01-VAXS121 | VENT | 01-0.75"-AXS1503-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 729 | PD-123A
01-VAXS122 | INSTRUMENT | 01-0.75"-AXS1013-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 730 | PD-050A
01-VAXS123 | FG STARTUP FEEDWATER HX OUTLET CHECK VALVE | 01-2"-AXS1504-1DAA1A-1.0 "EOH | 2" | Check valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | SWING CHECK | 731 | PD-123A
01-VAXS124 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE ISOLATION | 01-2"-AXS1504-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 732 | PD-123A
01-VAXS125 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE ISOLATION | 01-2"-AXS1505-1DCA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DCA1A | Steam/Water | CL800 | SWE | SWE | 425 | 470 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 733 | PD-123A
01-VAXS126 | DRAIN | 01-0.75"-AXS1504-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 734 | PD-123A
01-VAXS127 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE BYPASS | 01-0.75"-AXS1029-1DCA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DCA1A | Steam/Water | CL300 | SWE | SWE | 425 | 470 | S-40S | 1.0 " | Yes | 94.03.68.150.06.3H | THROTTLING SERVICE | 735 | PD-123A
01-VAXS129 | TRAP BYPASS | 01-0.75"-AXS1010-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 736 | PD-122A
01-VAXS130 | DRIP LEG DRAIN | 01-2"-AXS1012-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 737 | PD-122A
01-VAXS132 | VENT | 01-0.75"-AXS1078-1DAA1A-1.5 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 738 | PD-123A
01-VAXS133 | VENT | 01-0.75"-AXS1513-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 739 | PD-122A
01-VAXS135 | TRAP ISOLATION | 01-0.75"-AXS1237-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 740 | PD-122A
01-VAXS136 | TRAP ISOLATION | 01-0.75"-AXS1237-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 741 | PD-122A
01-VAXS137 | DRAIN | 01-0.75"-AXS1237-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 742 | PD-122A
01-VAXS138 | TRAP BYPASS | 01-0.75"-AXS1252-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 743 | PD-122A
01-VAXS144 | DRAIN | 01-0.75"-AXS1001-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 744 | PD-122A
01-VAXS145 | ACC SPRAGING MODULATING CONTROL VALVE BYPASS | 01-2.5"-AXS1097-1DAA1A-1.0 "EOC | 2.5" | Globe valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.0 " | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 745 | PD-050A
01-VAXS147 | DRAIN | 01-0.75"-AXS1509-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 746 | PD-050A
01-VAXS148 | SEAL STEAM REGULATION VALVE ISOLATION | 01-3"-AXS1511-1DAA1A-3.0 "EIC | 3" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 725 | S-40 | 3.0 " | No | 94.03.68.150.03.2H | FLEXIBLE WEDGE, EXTERNAL BYPASS VALVE | 747 | PD-300A
01-VAXS149 | SEAL STEAM REGULATION VALVE ISOLATION | 01-4"-AXS1511-1DAA1A-3.0 "EIC | 4" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 725 | S-40 | 3.0 " | No | 94.03.68.150.03.2H | FLEXIBLE WEDGE, EXTERNAL BYPASS VALVE | 748 | PD-300A
01-VAXS152 | DA EJECTOR SUPPLY CONTROL VALVE BYPASS | 01-1"-AXS1058-1DAA1A-1.0 "EOH | 1" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 749 | PD-050A
01-VAXS153 | DRAIN | 01-0.75"-AXS1508-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 750 | PD-050A
01-VAXS155 | DRIP LEG DRAIN | 01-2"-AXS1006-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 751 | PD-122A
01-VAXS156 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE BYPASS | 01-2"-AXS1020-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 752 | PD-123A
01-VAXS157 | INSTRUMENT | 01-0.75"-AXS1504-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 753 | PD-123A
01-VAXS158 | INSTRUMENT | 01-0.75"-AXS1503-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 754 | PD-123A
01-VAXS159 | SUPERHEATER/SEPARATOR ISOLATION | 01-3"-AXS1078-1DAA1A-1.5 "EIC | 3" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.150.03.0 | FLEXIBLE WEDGE, EXTERNAL BYPASS VALVE | 755 | PD-123A
01-VAXS160 | DRAIN | 01-0.75"-AXS1015-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 756 | PD-122A
01-VAXS161 | TRAP ISOLATION | 01-0.75"-AXS1015-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 757 | PD-122A
01-VAXS164 | TRAP BYPASS | 01-0.75"-AXS1014-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 758 | PD-122A
01-VAXS165 | ACC SPRAGING MODULATING CONTROL VALVE ISOLATION | 01-8"-AXS1047-1DAA1A-2.0 "EOH | 8" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 2.0 " | Yes | 94.03.68.150.03.0 | FLEXIBLE WEDGE, 3-WAY DRAIN | 759 | PD-050A
01-VAXS166 | TRAP ISOLATION | 01-0.75"-AXS1024-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 760 | PD-123A
01-VAXS167 | TRAP BYPASS | 01-0.75"-AXS1025-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 761 | PD-123A
01-VAXS168 | ACC SPARGING MODULATING CONTROL VALVE ISOLATION | 01-6"-AXS1507-1DAA1A-1.5 "EOC | 6" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.150.03.0 | FLEXIBLE WEDGE, 3-WAY DRAIN | 762 | PD-050A
01-VAXS171 | FG STARTUP FEEDWATER HX/ SEPARATOR ISOLATION | 01-3"-AXS1070-1DAA1A-1.5 "EOC | 3" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.150.03.0 | FLEXIBLE WEDGE, EXTERNAL BYPASS VALVE | 763 | PD-123A
01-VAXS174 | DA EJECTOR CONTROL VALVE ISOLATION | 01-2"-AXS1508-1DAA1A-1.0 "EOC | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 764 | PD-050A
01-VAXS175 | DA EJECTOR CONTROL VALVE ISOLATION | 01-2"-AXS1048-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 765 | PD-050A
01-VAXS182 | VENT | 01-1"-AXS1075-1DAA1A-1.0 "EOC | 1" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 766 | PD-050A
01-VAXS183 | VENT | 01-0.75"-AXS1048-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 767 | PD-050A
01-VAXS186 | INSTRUMENT | 01-0.75"-AXS1048-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 768 | PD-050A
01-VAXS187 | INSTRUMENT | 01-0.75"-AXS1500-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 769 | PD-123A
01-VAXS188 | INSTRUMENT | 01-0.75"-AXS1500-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 770 | PD-123A
01-VAXS189 | TRAP ISOLATION | 01-0.75"-AXS1001-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 771 | PD-122A
01-VAXS190 | TRAP ISOLATION | 01-2"-AXS1071-1DAA1A-1.5 "EIC | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 772 | PD-123A
01-VAXS191 | TRAP BYPASS | 01-0.75"-AXS1073-1DAA1A-1.5 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 773 | PD-123A
01-VAXS194 | TRAP ISOLATION | 01-0.75"-AXS1073-1DAA1A-1.5 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 774 | PD-123A
01-VAXS195 | DRAIN | 01-0.75"-AXS1073-1DAA1A-1.5 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 775 | PD-123A
01-VAXS196 | SEAL STEAM CONTROL VALVE WARMING LINE ISOLATION | 01-0.75"-AXS1079-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 776 | PD-123A
01-VAXS197 | SEAL STEAM CONTROL VALVE WARMING LINE THROTTLING | 01-0.75"-AXS1079-1DAA1A-2.0 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 777 | PD-123A
01-VAXS198 | SEAL STEAM CONTROL VALVE WARMING LINE ISOLATION | 01-0.75"-AXS1079-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 778 | PD-123A
01-VAXS199 | DRIP LEG DRAIN | 01-2"-AXS1027-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 779 | PD-123A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 780 | P&ID
01-VAXS200 | DRIP LEG DRAIN | 01-2"-AXS1124-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 781 | PD-123A
01-VAXS201 | TRAP ISOLATION | 01-0.75"-AXS1132-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 782 | PD-123A
01-VAXS202 | TRAP BYPASS | 01-0.75"-AXS1076-1DAA1A-1.5 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 783 | PD-123A
01-VAXS203 | DRAIN | 01-0.75"-AXS1024-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 784 | PD-123A
01-VAXS204 | SEAL STEAM REGULATING VALVE BYPASS | 01-2"-AXS1654-1DAA1A-2.5 "EIC | 2" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.5 " | No | 94.03.68.150.06.2H | THROTTLING SERVICE | 785 | PD-300A
01-VAXS289 | TRAP BYPASS | 01-0.75"-AXS1003-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 786 | PD-122A
01-VAXS290 | TRAP ISOLATION | 01-0.75"-AXS1001-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 787 | PD-122A
01-VAXS291 | DRIP LEG DRAIN | 01-2"-AXS1008-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 788 | PD-122A
01-VBDN100 | INSTRUMENT ROOT VALVE | 01-0.5"-BDN1014-1BAA2A-1.0 "MOH | 0.5" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 789 | PD-090A
01-VBDN101 | INSTRUMENT ROOT VALVE | 01-0.5"-BDN1014-1BAA2A-1.0 "MOH | 0.5" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 790 | PD-090A
01-VBDN112 | VENT ROOT VALVE | 01-0.75"-BDN1024-1BAA2A-1.0 "MOH | 0.75" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 791 | PD-090A
01-VBDN119 | UNIT 1 BDN PUMP B DISCHARGE CHECK | 01-8"-BDN1682-1BAA2A-1.0 "MOH | 8" | Check valve | BDN | 1BAA2A | Water | CL150 | WAFER | WAFER | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | DUAL PLATE; MAX FLOW - 1600 GPM, MIN FLOW - 180 GPM | 792 | PD-090A
01-VBDN120 | UNIT 1 BDN PUMP A DISCHARGE CHECK | 01-8"-BDN1024-1BAA2A-1.0 "MOH | 8" | Check valve | BDN | 1BAA2A | Water | CL150 | WAFER | WAFER | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | DUAL PLATE; MAX FLOW - 1600 GPM, MIN FLOW - 180 GPM | 793 | PD-090A
01-VBDN123 | UNIT 1 BDN PUMP B DISCHARGE ISOLATION | 01-8"-BDN1682-1BAA2A-1.0 "MOH | 8" | Butterfly valve | BDN | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 794 | PD-090A
01-VBDN124 | UNIT 1 BDN PUMP A DISCHARGE ISOLATION | 01-8"-BDN1024-1BAA2A-1.0 "MOH | 8" | Butterfly valve | BDN | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 795 | PD-090A
01-VBFW101 | DRAIN VALVE | 01-1"-BFW1070-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 796 | PD-062A
01-VBFW103 | HRH TA SPRAY DRAIN | 01-0.75"-BFW1274-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 797 | PD-034A
01-VBFW105 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 01-6"-BFW1105-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 798 | PD-062A
01-VBFW106 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 01-6"-BFW1006-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 799 | PD-062A
01-VBFW107 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 01-6"-BFW1006-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 800 | PD-062A
01-VBFW108 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 01-6"-BFW1006-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 801 | PD-062A
01-VBFW109 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 01-6"-BFW1105-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 802 | PD-062A
01-VBFW110 | VENT VALVE | 01-0.75"-BFW1010-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 803 | PD-064A
01-VBFW111 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 01-6"-BFW1006-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 804 | PD-062A
01-VBFW112 | INSTRUMENT ISOLATION | 01-0.5"-BFW1025-1FAC1A-1.0 "EOH | 0.5" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 805 | PD-020A
01-VBFW113 | STRAINER DRAIN | 01-1"-BFW1077-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 806 | PD-062A
01-VBFW114 | INSTRUMENT ISOLATION | 01-0.5"-BFW1035-1FAC1A-1.0 "EOH | 0.5" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 807 | PD-020A
01-VBFW115 | STRAINER DRAIN | 01-1"-BFW1070-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 808 | PD-062A
01-VBFW116 | DRAIN VALVE | 01-1"-BFW1608-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 809 | PD-061A
01-VBFW117 | VENT VALVE | 01-0.75"-BFW1010-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 810 | PD-064A
01-VBFW118 | HRH TA SPRAY SUPPLY ISOLATION | 01-3"-BFW1108-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE | 811 | PD-034A
01-VBFW119 | DRAIN VALVE | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 812 | PD-020A
01-VBFW120 | DRAIN VALVE | 01-0.75"-BFW1011-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 813 | PD-064A
01-VBFW121 | DRAIN VALVE | 01-0.75"-BFW1011-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 814 | PD-064A
01-VBFW123 | DRAIN VALVE | 01-1"-BFW1408-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 815 | PD-062A
01-VBFW128 | HPS BYPASS SPRAY ISOLATION | 01-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 816 | PD-062A
01-VBFW129 | HPS BYPASS SPRAY ISOLATION | 01-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 817 | PD-062A
01-VBFW130 | DRAIN VALVE | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 818 | PD-062A
01-VBFW131 | DRAIN VALVE | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 819 | PD-062A
01-VBFW132 | INSTRUMENT ISOLATION | 01-0.75"-BFW1019-1DAA1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1DAA1A | Water | CL800 | SWE | SWE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 820 | PD-060A
01-VBFW138 | DRAIN VALVE | 01-0.75"-BFW1018-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 821 | PD-061A
01-VBFW139 | DRAIN VALVE | 01-0.75"-BFW1018-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 822 | PD-061A
01-VBFW140 | INSTRUMENT ISOLATION | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 823 | PD-124A
01-VBFW141 | INSTRUMENT ISOLATION | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 824 | PD-124A
01-VBFW142 | INSTRUMENT ISOLATION | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 825 | PD-124A
01-VBFW143 | INSTRUMENT ISOLATION | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 826 | PD-124A
01-VBFW144 | DRAIN VALVE | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 827 | PD-124A
01-VBFW145 | DRAIN VALVE | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 828 | PD-124A
01-VBFW146 | CRH LETDOWN SPRAY SUPPLY ISOLATION | 01-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 829 | PD-124A
01-VBFW147 | VENT VALVE | 01-0.75"-BFW1018-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 830 | PD-061A
01-VBFW148 | CRH LETDOWN SPRAY SUPPLY CHECK | 01-1"-BFW1383-1FAC1A-1.0 "EOH | 1" | Check valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | PISTON CHECK | 831 | PD-124A
01-VBFW149 | DRAIN VALVE | 01-1"-BFW1019-1DAA1A-1.0 "EOH | 1" | Gate valve | BFW | 1DAA1A | Water | CL800 | SWE | SWE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 832 | PD-060A
01-VBFW150 | VENT VALVE | 01-0.75"-BFW1018-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 833 | PD-061A
01-VBFW151 | VENT VALVE | 01-1"-BFW1069-1FAC1A-1.0 "EOH | 1" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 834 | PD-062A
01-VBFW152 | BFW SUCTION LP DRUM ISOLATION | 01-12"-BFW1019-1DAA1A-1.0 "EOH | 12" | Gate valve | BFW | 1DAA1A | Water | CL600 | BE | BE | 300 | 360 | S-STD | 1.0 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 835 | PD-060A
01-VBFW153 | VENT VALVE | 01-0.75"-BFW1461-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 836 | PD-064A
01-VBFW154 | INSTRUMENT ISOLATION | 01-0.75"-BFW1019-1DAA1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1DAA1A | Water | CL800 | SWE | SWE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 837 | PD-060A
01-VBFW155 | INSTRUMENT ISOLATION | 01-0.75"-BFW1019-1DAA1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1DAA1A | Water | CL800 | SWE | SWE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 838 | PD-060A
01-VBFW156 | INSTRUMENT ISOLATION | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 839 | PD-124A
01-VBFW157 | INSTRUMENT ISOLATION | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 840 | PD-124A
01-VBFW161 | VENT VALVE | 01-1"-BFW1069-1FAC1A-1.0 "EOH | 1" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 841 | PD-062A
01-VBFW162 | INSTRUMENT ISOLATION | 01-1"-BFW1076-1FAC1A-1.0 "EOH | 1" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 842 | PD-062A
01-VBFW163 | INSTRUMENT ISOLATION | 01-1"-BFW1076-1FAC1A-1.0 "EOH | 1" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 843 | PD-062A
01-VBFW164 | CRH AUX STEAM DSH SPRAY CHECK | 01-1"-BFW1156-1FAC1A-1.0 "EOH | 1" | Check valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | PISTON CHECK | 844 | PD-124A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 845 | P&ID
01-VBFW165 | DRAIN VALVE | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 846 | PD-063A
01-VBFW166 | DRAIN VALVE | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 847 | PD-063A
01-VBFW167 | BFP A IP DISCHARGE CHECK | 01-6"-BFW1374-1FAC1A-1.5 "EOH | 6" | Check valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 900 GPM, MIN FLOW- 140 GPM | 848 | PD-060A
01-VBFW168 | DRAIN VALVE | 01-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 849 | PD-060A
01-VBFW169 | DRAIN VALVE | 01-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 850 | PD-060A
01-VBFW170 | INSTRUMENT ISOLATION | 01-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 851 | PD-060A
01-VBFW171 | INSTRUMENT ISOLATION | 01-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 852 | PD-060A
01-VBFW172 | VENT VALVE | 01-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 853 | PD-060A
01-VBFW173 | VENT VALVE | 01-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 854 | PD-060A
01-VBFW174 | BFP B IP DISCHARGE CHECK | 01-6"-BFW1063-1FAC1A-1.5 "EOH | 6" | Check valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 900 GPM, MIN FLOW- 140 GPM | 855 | PD-060A
01-VBFW175 | DRAIN VALVE | 01-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 856 | PD-060A
01-VBFW176 | DRAIN VALVE | 01-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 857 | PD-060A
01-VBFW177 | INSTRUMENT ISOLATION | 01-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 858 | PD-060A
01-VBFW178 | INSTRUMENT ISOLATION | 01-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 859 | PD-060A
01-VBFW181 | INSTRUMENT ISOLATION | 01-0.75"-BFW1033-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 860 | PD-061A
01-VBFW182 | INSTRUMENT ISOLATION | 01-0.75"-BFW1033-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 861 | PD-061A
01-VBFW183 | INSTRUMENT ISOLATION | 01-0.75"-BFW1044-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 862 | PD-061A
01-VBFW184 | INSTRUMENT ISOLATION | 01-0.75"-BFW1044-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 863 | PD-061A
01-VBFW185 | INSTRUMENT ISOLATION | 01-0.75"-BFW1045-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 864 | PD-061A
01-VBFW186 | INSTRUMENT ISOLATION | 01-0.75"-BFW1045-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 865 | PD-061A
01-VBFW187 | INSTRUMENT ISOLATION | 01-0.75"-BFW1053-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 866 | PD-061A
01-VBFW188 | INSTRUMENT ISOLATION | 01-0.75"-BFW1053-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 867 | PD-061A
01-VBFW189 | VENT VALVE | 01-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 868 | PD-061A
01-VBFW190 | VENT VALVE | 01-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 869 | PD-061A
01-VBFW191 | BFP A HP DISCHARGE CHECK | 01-10"-BFW1029-1HAC2A-1.5 "EOH | 10" | Check valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 2500 GPM, MIN FLOW- 840 GPM | 870 | PD-061A
01-VBFW192 | DRAIN VALVE | 01-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 871 | PD-061A
01-VBFW193 | DRAIN VALVE | 01-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 872 | PD-061A
01-VBFW194 | DRAIN VALVE | 01-1"-BFW1029-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 873 | PD-061A
01-VBFW195 | DRAIN VALVE | 01-1"-BFW1029-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 874 | PD-061A
01-VBFW196 | HP BFW FILL FROM CONDENSATE CHECK | 01-2"-BFW1608-1HAC2A-1.0 "EOH | 2" | Check valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | PISTON CHECK | 875 | PD-061A
01-VBFW197 | HP BFW FILL FROM CONDENSATE STOP CHECK | 01-2"-BFW1608-1HAC2A-1.0 "EOH | 2" | Check Valve Locked Closed | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | GLOBE STOP CHECK | 876 | PD-061A
01-VBFW198 | HP BFW FILL FROM CONDENSATE BLOCK | 01-2"-BFW1608-1HAC2A-1.0 "EOH | 2" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | FLOW UNDER PLUG | 877 | PD-061A
01-VBFW199 | INSTRUMENT ISOLATION | 01-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 878 | PD-061A
01-VBFW200 | INSTRUMENT ISOLATION | 01-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 879 | PD-061A
01-VBFW209 | VENT VALVE | 01-0.75"-BFW1073-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 880 | PD-061A
01-VBFW210 | VENT VALVE | 01-0.75"-BFW1073-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 881 | PD-061A
01-VBFW211 | DRAIN VALVE | 01-0.75"-BFW1059-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 882 | PD-061A
01-VBFW212 | DRAIN VALVE | 01-0.75"-BFW1059-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 883 | PD-061A
01-VBFW213 | VENT VALVE | 01-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 884 | PD-061A
01-VBFW214 | VENT VALVE | 01-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 885 | PD-061A
01-VBFW215 | BFP A MIN RECIRC STRAINER ISOLATION | 01-6"-BFW1064-1HAC2A-1.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, EXTERNAL BONNET DRAIN | 886 | PD-061A
01-VBFW216 | STRAINER DRAIN | 01-1.5"-BFW1031-1HAC2A-1.0 "EOH | 1.5" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 887 | PD-061A
01-VBFW217 | STRAINER DRAIN | 01-1.5"-BFW1031-1HAC2A-1.0 "EOH | 1.5" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 888 | PD-061A
01-VBFW218 | BFP A MIN RECIRC ACC ISOLATION | 01-6"-BFW1066-1HBB1A-1.5 "EOH | 6" | Ball valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 370 | 0.808" min | 1.5 " | Yes | 94.03.68.150.08.0 | FULL PORT, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED, 8" OPERATOR MOUNTING KIT | 889 | PD-061A
01-VBFW219 | INSTRUMENT ISOLATION | 01-0.75"-BFW1060-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 890 | PD-061A
01-VBFW220 | INSTRUMENT ISOLATION | 01-0.75"-BFW1060-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 891 | PD-061A
01-VBFW221 | INSTRUMENT ISOLATION | 01-0.75"-BFW1061-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 892 | PD-061A
01-VBFW222 | INSTRUMENT ISOLATION | 01-0.75"-BFW1061-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 893 | PD-061A
01-VBFW223 | INSTRUMENT ISOLATION | 01-0.75"-BFW1062-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 894 | PD-061A
01-VBFW224 | INSTRUMENT ISOLATION | 01-0.75"-BFW1062-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 895 | PD-061A
01-VBFW225 | INSTRUMENT ISOLATION | 01-0.75"-BFW1068-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 896 | PD-061A
01-VBFW226 | INSTRUMENT ISOLATION | 01-0.75"-BFW1068-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 897 | PD-061A
01-VBFW227 | VENT VALVE | 01-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 898 | PD-061A
01-VBFW228 | VENT VALVE | 01-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 899 | PD-061A
01-VBFW229 | BFP B HP DISCHARGE CHECK | 01-10"-BFW1052-1HAC2A-1.5 "EOH | 10" | Check valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 2500 GPM, MIN FLOW- 840 GPM | 900 | PD-061A
01-VBFW230 | VENT VALVE | 01-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 901 | PD-061A
01-VBFW231 | VENT VALVE | 01-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 902 | PD-061A
01-VBFW232 | BFP B MIN RECIRC STRAINER ISOLATION | 01-6"-BFW1072-1HAC2A-1.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, EXTERNAL BONNET DRAIN | 903 | PD-061A
01-VBFW233 | STRAINER DRAIN | 01-1.5"-BFW1058-1HAC2A-1.0 "EOH | 1.5" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 904 | PD-061A
01-VBFW234 | STRAINER DRAIN | 01-1.5"-BFW1058-1HAC2A-1.0 "EOH | 1.5" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 905 | PD-061A
01-VBFW235 | DRAIN VALVE | 01-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 906 | PD-061A
01-VBFW236 | DRAIN VALVE | 01-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 907 | PD-061A
01-VBFW237 | DRAIN VALVE | 01-1"-BFW1052-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 908 | PD-061A
01-VBFW238 | DRAIN VALVE | 01-1"-BFW1052-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 909 | PD-061A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 910 | P&ID
01-VBFW239 | BFP B MIN RECIRC ACC ISOLATION | 01-6"-BFW1074-1HBB1A-1.5 "EOH | 6" | Ball valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 370 | 0.808" min | 1.5 " | Yes | 94.03.68.150.08.0 | FULL PORT, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED, 8" OPERATOR MOUNTING KIT | 911 | PD-061A
01-VBFW240 | DRAIN VALVE | 01-0.75"-BFW1149-1HBD1A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HBD1A | Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 912 | PD-020A
01-VBFW241 | DRAIN VALVE | 01-0.75"-BFW1149-1HBD1A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HBD1A | Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 913 | PD-020A
01-VBFW242 | INSTRUMENT ISOLATION | 01-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 914 | PD-020A
01-VBFW243 | INSTRUMENT ISOLATION | 01-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 915 | PD-020A
01-VBFW244 | INSTRUMENT ISOLATION | 01-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 916 | PD-020A
01-VBFW245 | INSTRUMENT ISOLATION | 01-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 917 | PD-020A
01-VBFW246 | VENT VALVE | 01-1"-BFW1000-1HAC2A-1.0 "EOH | 1" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 918 | PD-020A
01-VBFW247 | VENT VALVE | 01-1"-BFW1000-1HAC2A-1.0 "EOH | 1" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 919 | PD-020A
01-VBFW248 | VENT VALVE | 01-1"-BFW1007-1HAC2A-1.0 "EOH | 1" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 920 | PD-020A
01-VBFW249 | VENT VALVE | 01-1"-BFW1007-1HAC2A-1.0 "EOH | 1" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 921 | PD-020A
01-VBFW250 | INSTRUMENT ISOLATION | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 922 | PD-062A
01-VBFW251 | INSTRUMENT ISOLATION | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 923 | PD-062A
01-VBFW252 | INSTRUMENT ISOLATION | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 924 | PD-062A
01-VBFW253 | INSTRUMENT ISOLATION | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 925 | PD-062A
01-VBFW254 | INSTRUMENT ISOLATION | 01-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 926 | PD-061A
01-VBFW255 | INSTRUMENT ISOLATION | 01-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 927 | PD-061A
01-VBFW256 | INSTRUMENT ISOLATION | 01-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 928 | PD-061A
01-VBFW257 | INSTRUMENT ISOLATION | 01-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 929 | PD-061A
01-VBFW258 | INSTRUMENT ISOLATION | 01-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 930 | PD-061A
01-VBFW259 | INSTRUMENT ISOLATION | 01-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 931 | PD-061A
01-VBFW260 | INSTRUMENT ISOLATION | 01-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 932 | PD-061A
01-VBFW261 | INSTRUMENT ISOLATION | 01-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 933 | PD-061A
01-VBFW262 | INSTRUMENT ISOLATION | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 934 | PD-064A
01-VBFW263 | BFP SUCTION FROM LPEC BYPASS CHECK | 01-8"-BFW1021-1EAA1A-1.0 "EOH | 8" | Check valve | BFW | 1EAA1A | Water | CL600 | BE | BE | 790 | 360 | S-40 | 1.0 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 2400 GPM, MIN FLOW- 840 GPM | 935 | PD-060A
01-VBFW264 | BFP SUCTION ISOLATION FROM LPEC BYPASS | 01-8"-BFW1021-1EAA1A-1.0 "EOH | 8" | Gate valve | BFW | 1EAA1A | Water | CL600 | BE | BE | 790 | 360 | S-40 | 1.0 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 936 | PD-060A
01-VBFW265 | BFP A SUCTION ISOLATION | 01-12"-BFW1020-1DAA1A-1.0 "EOH | 12" | Gate valve | BFW | 1DAA1A | Water | CL600 | BE | BE | 300 | 360 | S-STD | 1.0 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 937 | PD-060A
01-VBFW266 | BFP B SUCTION ISOLATION | 01-12"-BFW1038-1DAA1A-1.0 "EOH | 12" | Gate valve | BFW | 1DAA1A | Water | CL600 | BE | BE | 300 | 360 | S-STD | 1.0 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 938 | PD-060A
01-VBFW267 | DRAIN VALVE | 01-0.75"-BFW1073-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 939 | PD-061A
01-VBFW269 | BFP A IP DISCHARGE ISOLATION | 01-6"-BFW1374-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 940 | PD-060A
01-VBFW270 | BFP B IP DISCHARGE ISOLATION | 01-6"-BFW1063-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 941 | PD-060A
01-VBFW271 | BFP A HP DISCHARGE ISOLATION | 01-10"-BFW1029-1HAC2A-1.5 "EOH | 10" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 942 | PD-061A
01-VBFW272 | BFP B HP DISCHARGE ISOLATION | 01-10"-BFW1052-1HAC2A-1.5 "EOH | 10" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 943 | PD-061A
01-VBFW273 | INSTRUMENT ISOLATION | 01-0.75"-BFW1457-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 944 | PD-064A
01-VBFW274 | INSTRUMENT ISOLATION | 01-0.75"-BFW1459-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 945 | PD-064A
01-VBFW275 | INSTRUMENT ISOLATION | 01-0.75"-BFW1456-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 946 | PD-064A
01-VBFW276 | INSTRUMENT ISOLATION | 01-0.75"-BFW1460-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 947 | PD-064A
01-VBFW277 | VENT VALVE | 01-0.75"-BFW1434-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 948 | PD-064A
01-VBFW278 | INSTRUMENT ISOLATION | 01-0.75"-BFW1485-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 949 | PD-064A
01-VBFW279 | INSTRUMENT ISOLATION | 01-0.75"-BFW1453-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 950 | PD-064A
01-VBFW280 | INSTRUMENT ISOLATION | 01-0.75"-BFW1443-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 951 | PD-064A
01-VBFW281 | INSTRUMENT ISOLATION | 01-0.75"-BFW1479-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 952 | PD-064A
01-VBFW282 | INSTRUMENT ISOLATION | 01-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 953 | PD-064A
01-VBFW283 | VENT VALVE | 01-0.75"-BFW1041-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 954 | PD-064A
01-VBFW284 | INSTRUMENT ISOLATION | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 955 | PD-064A
01-VBFW285 | N2 CONNECTION | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 956 | PD-064A
01-VBFW286 | DRAIN VALVE | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 957 | PD-064A
01-VBFW287 | INSTRUMENT ISOLATION | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 958 | PD-064A
01-VBFW288 | INSTRUMENT ISOLATION | 01-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 959 | PD-064A
01-VBFW289 | DRAIN VALVE | 01-0.75"-BFW1434-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 960 | PD-064A
01-VBFW290 | FGH OUTLET RECIRC CV ISOLATION | 01-4"-BFW1442-1FAC1A-1.0 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 961 | PD-064A
01-VBFW291 | DRAIN VALVE | 01-0.75"-BFW1008-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 962 | PD-064A
01-VBFW292 | STRAINER DRAIN | 01-0.75"-BFW1094-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 963 | PD-064A
01-VBFW293 | INSTRUMENT ISOLATION | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 964 | PD-064A
01-VBFW294 | DRAIN VALVE | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 965 | PD-063A
01-VBFW295 | INSTRUMENT ISOLATION | 01-0.75"-BFW1079-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 966 | PD-063A
01-VBFW296 | INSTRUMENT ISOLATION | 01-0.75"-BFW1080-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 967 | PD-063A
01-VBFW297 | INSTRUMENT ISOLATION | 01-0.75"-BFW1080-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 968 | PD-063A
01-VBFW298 | INSTRUMENT ISOLATION | 01-0.75"-BFW1081-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 969 | PD-063A
01-VBFW299 | INSTRUMENT ISOLATION | 01-0.75"-BFW1081-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 970 | PD-063A
01-VBFW300 | CT TCA COOLER BFW INLET ISOLATION | 01-6"-BFW1028-1HAC2A-1.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 971 | PD-063A
01-VBFW301 | DRAIN VALVE | 01-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 972 | PD-063A
01-VBFW302 | DRAIN VALVE | 01-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 973 | PD-063A
01-VBFW303 | DRAIN VALVE | 01-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 974 | PD-063A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 975 | P&ID
01-VBFW304 | DRAIN VALVE | 01-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 976 | PD-063A
01-VBFW305 | DRAIN VALVE | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 977 | PD-063A
01-VBFW306 | CT TCA COOLER BFW OUTLET ISOLATION | 01-6"-BFW1320-1HAC2A-2.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 978 | PD-063A
01-VBFW307 | INSTRUMENT ISOLATION | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 979 | PD-063A
01-VBFW308 | INSTRUMENT ISOLATION | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 980 | PD-063A
01-VBFW309 | INSTRUMENT ISOLATION | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 981 | PD-063A
01-VBFW310 | INSTRUMENT ISOLATION | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 982 | PD-063A
01-VBFW311 | INSTRUMENT ISOLATION | 01-0.75"-BFW1082-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 983 | PD-063A
01-VBFW312 | INSTRUMENT ISOLATION | 01-0.75"-BFW1082-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 984 | PD-063A
01-VBFW313 | INSTRUMENT ISOLATION | 01-0.75"-BFW1083-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 985 | PD-063A
01-VBFW314 | INSTRUMENT ISOLATION | 01-0.75"-BFW1083-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 986 | PD-063A
01-VBFW315 | INSTRUMENT ISOLATION | 01-0.75"-BFW1084-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 987 | PD-063A
01-VBFW316 | INSTRUMENT ISOLATION | 01-0.75"-BFW1084-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 988 | PD-063A
01-VBFW317 | INSTRUMENT ISOLATION | 01-0.75"-BFW1085-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 989 | PD-063A
01-VBFW318 | INSTRUMENT ISOLATION | 01-0.75"-BFW1085-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 990 | PD-063A
01-VBFW319 | CRH LETDOWN SPRAY ISOLATION | 01-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 991 | PD-124A
01-VBFW320 | INSTRUMENT ISOLATION | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 992 | PD-063A
01-VBFW321 | INSTRUMENT ISOLATION | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 993 | PD-063A
01-VBFW322 | VENT VALVE | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 994 | PD-063A
01-VBFW323 | VENT VALVE | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 995 | PD-063A
01-VBFW324 | VENT VALVE | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 996 | PD-063A
01-VBFW325 | VENT VALVE | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 997 | PD-063A
01-VBFW326 | INSTRUMENT ISOLATION | 01-0.75"-BFW1324-1HBB1A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HBB1A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H |  | 998 | PD-063A
01-VBFW327 | INSTRUMENT ISOLATION | 01-0.75"-BFW1324-1HBB1A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HBB1A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H |  | 999 | PD-063A
01-VBFW328 | DRAIN VALVE | 01-0.75"-BFW1324-1HBB1A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HBB1A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1000 | PD-063A
01-VBFW329 | DRAIN VALVE | 01-0.75"-BFW1324-1HBB1A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HBB1A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1001 | PD-063A
01-VBFW330 | CT TCA COOLER BFW ISOLATION TO RECIRC | 01-6"-BFW1322-1HAC2A-2.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1002 | PD-063A
01-VBFW331 | VENT VALVE | 01-0.75"-BFW1040-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1003 | PD-063A
01-VBFW332 | VENT VALVE | 01-0.75"-BFW1040-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1004 | PD-063A
01-VBFW333 | DRAIN VALVE | 01-0.75"-BFW1087-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1005 | PD-063A
01-VBFW334 | DRAIN VALVE | 01-0.75"-BFW1087-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1006 | PD-063A
01-VBFW335 | DRAIN VALVE | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1007 | PD-063A
01-VBFW336 | DRAIN VALVE | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1008 | PD-063A
01-VBFW337 | DRAIN VALVE | 01-0.75"-BFW1073-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1009 | PD-061A
01-VBFW338 | DRAIN VALVE | 01-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1010 | PD-061A
01-VBFW339 | CT TCA COOLER RECIRC ACC ISOLATION | 01-6"-BFW1426-1HBB1A-2.5 "EOH | 6" | Ball valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 705 | 0.808" min | 2.5 " | Yes | 94.03.68.150.08.0 | FULL PORT, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED, 8" OPERATOR MOUNTING KIT | 1011 | PD-063A
01-VBFW340 | INSTRUMENT ISOLATION | 01-0.75"-BFW1088-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1012 | PD-064A
01-VBFW341 | INSTRUMENT ISOLATION | 01-0.75"-BFW1088-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1013 | PD-064A
01-VBFW342 | INSTRUMENT ISOLATION | 01-0.75"-BFW1089-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1014 | PD-064A
01-VBFW343 | INSTRUMENT ISOLATION | 01-0.75"-BFW1089-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1015 | PD-064A
01-VBFW344 | FG HX AUTOMATIC BLOCK VALVE ISOLATION | 01-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1016 | PD-064A
01-VBFW345 | FG HX AUTOMATIC BLOCK VALVE ISOLATION | 01-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1017 | PD-064A
01-VBFW346 | FG HX WARMING VALVE ISOLATION | 01-1"-BFW1454-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1018 | PD-064A
01-VBFW347 | FG HX WARMING VALVE ISOLATION | 01-1"-BFW1454-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1019 | PD-064A
01-VBFW348 | N2 PURGE CONNECTION | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1020 | PD-064A
01-VBFW349 | VENT VALVE | 01-0.75"-BFW1041-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1021 | PD-064A
01-VBFW350 | FG HX BFW UPSTREAM ISOLATION | 01-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1022 | PD-064A
01-VBFW351 | DRAIN VALVE | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1023 | PD-064A
01-VBFW352 | FG HX BFW UPSTREAM ISOLATION | 01-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1024 | PD-064A
01-VBFW353 | FG HX LEAK DETECTION VENT | 01-0.75"-BFW1461-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1025 | PD-064A
01-VBFW354 | INSTRUMENT ISOLATION | 01-0.75"-BFW1456-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1026 | PD-064A
01-VBFW355 | INSTRUMENT ISOLATION | 01-0.75"-BFW1460-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1027 | PD-064A
01-VBFW356 | INSTRUMENT ISOLATION | 01-0.75"-BFW1457-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1028 | PD-064A
01-VBFW357 | INSTRUMENT ISOLATION | 01-0.75"-BFW1459-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1029 | PD-064A
01-VBFW359 | INSTRUMENT ISOLATION | 01-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1030 | PD-064A
01-VBFW360 | DRAIN VALVE | 01-0.75"-BFW1434-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1031 | PD-064A
01-VBFW361 | FG HX RECIRC ISOLATION | 01-4"-BFW1442-1FAC1A-1.0 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1032 | PD-064A
01-VBFW362 | DRAIN VALVE | 01-0.75"-BFW1009-1FBD1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FBD1A | Water | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1033 | PD-034A
01-VBFW363 | DRAIN VALVE | 01-0.75"-BFW1009-1FBD1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FBD1A | Water | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1034 | PD-034A
01-VBFW364 | DRAIN VALVE | 01-0.75"-BFW1008-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1035 | PD-064A
01-VBFW365 | DRAIN VALVE | 01-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.2H | WEDGE GATE | 1036 | PD-061A
01-VBFW366 | DRAIN VALVE | 01-0.75"-BFW1094-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1037 | PD-064A
01-VBFW367 | FG HX OUTLET ISOLATION TO CND | 01-4"-BFW1008-1FAC1A-1.0 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1038 | PD-064A
01-VBFW368 | FG HX OUTLET TO CND CHECK | 01-4"-BFW1067-1EAA1A-1.0 "EOH | 4" | Check valve | BFW | 1EAA1A | Water | CL600 | BE | BE | 790 | 589 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; MAX FLOW 230 GPM, MIN FLOW 15 GPM | 1039 | PD-064A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1040 | P&ID
01-VBFW369 | FG HX LEAK DETECTION VENT | 01-0.75"-BFW1434-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1041 | PD-064A
01-VBFW370 | INSTRUMENT ISOLATION | 01-0.75"-BFW1443-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1042 | PD-064A
01-VBFW371 | INSTRUMENT ISOLATION | 01-0.75"-BFW1479-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1043 | PD-064A
01-VBFW372 | INSTRUMENT ISOLATION | 01-0.75"-BFW1485-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1044 | PD-064A
01-VBFW373 | INSTRUMENT ISOLATION | 01-0.75"-BFW1453-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1045 | PD-064A
01-VBFW374 | HPS TA SPRAY SUPPLY CHECK | 01-3"-BFW1149-1HBD1A-2.0 "EOH | 3" | Check valve | BFW | 1HBD1A | Water | CL2500 SPL | BE | BE | 2534 | 1097 | S-XXS | 2.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; MAX FLOW 215 GPM, MIN FLOW 50 GPM | 1046 | PD-020A
01-VBFW375 | HPS TA SPRAY STRAINER ISOLATION | 01-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1047 | PD-020A
01-VBFW376 | HPS TA SPRAY STRAINER ISOLATION | 01-3"-BFW1153-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1048 | PD-020A
01-VBFW377 | DRAIN VALVE | 01-1"-BFW1012-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1049 | PD-020A
01-VBFW378 | INSTRUMENT ISOLATION | 01-0.5"-BFW1025-1FAC1A-1.0 "EOH | 0.5" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1050 | PD-020A
01-VBFW379 | FG HX OUTLET RECIRC CV OUTLET ISOLATION | 01-4"-BFW1093-1FBB1A-EOH | 4" | Ball valve | BFW | 1FBB1A | Water | CL1500 | BE | BE | 1400 | 589 | S-80 |  | Yes | 94.03.68.150.08.0 | FULL PORT, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED | 1051 | PD-064A
01-VBFW380 | STRAINER DRAIN | 01-1"-BFW1001-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1052 | PD-020A
01-VBFW381 | DRAIN VALVE | 01-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1053 | PD-061A
01-VBFW382 | DRAIN VALVE | 01-0.75"-BFW1067-1EAA1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1EAA1A | Water | CL800 | SWE | SWE | 790 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1054 | PD-053A
01-VBFW383 | HPS TA SPRAY STRAINER ISOLATION | 01-3"-BFW1153-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1055 | PD-020A
01-VBFW384 | INSTRUMENT ISOLATION | 01-0.75"-BFW1079-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1056 | PD-063A
01-VBFW386 | INSTRUMENT ISOLATION | 01-0.75"-BFW1078-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1057 | PD-063A
01-VBFW387 | DRAIN VALVE | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1058 | PD-020A
01-VBFW388 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 01-6"-BFW1105-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1059 | PD-062A
01-VBFW389 | HRH TA SPRAY SUPPLY DRAIN | 01-0.75"-BFW1274-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1060 | PD-034A
01-VBFW390 | STRAINER DRAIN | 01-1"-BFW1077-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1061 | PD-062A
01-VBFW391 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 01-6"-BFW1105-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1062 | PD-062A
01-VBFW392 | HRH TA SPRAY SUPPLY CHECK | 01-3"-BFW1009-1FBD1A-1.5 "EOH | 3" | Check valve | BFW | 1FBD1A | Water | CL900 | BE | BE | 586 | 1096 | S-40 | 1.5 " | Yes | 94.03.68.150.01.1H | TILTING DISC; MAX FLOW 250 GPM, MIN FLOW 50 GPM | 1063 | PD-034A
01-VBFW402 | DRAIN VALVE | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1064 | PD-064A
01-VBFW403 | DRAIN VALVE | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1065 | PD-064A
01-VBFW404 | INSTRUMENT ISOLATION | 01-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 1066 | PD-060A
01-VBFW405 | INSTRUMENT ISOLATION | 01-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 1067 | PD-060A
01-VBFW406 | INSTRUMENT ISOLATION | 01-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 1068 | PD-060A
01-VBFW407 | INSTRUMENT ISOLATION | 01-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 1069 | PD-060A
01-VBFW408 | IP BFW FILL FROM CONDENSATE CHECK | 01-2"-BFW1408-1FAC1A-1.0 "EOH | 2" | Check valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | PISTON CHECK | 1070 | PD-062A
01-VBFW409 | IP BFW FILL FROM CONDENSATE STOP CHECK | 01-2"-BFW1408-1FAC1A-1.0 "EOH | 2" | Check Valve Locked Closed | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | GLOBE STOP CHECK | 1071 | PD-062A
01-VBFW410 | IP BFW FILL FROM CONDENSATE BLOCK | 01-2"-BFW1408-1FAC1A-1.0 "EOH | 2" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | FLOW UNDER PLUG | 1072 | PD-062A
01-VBFW411 | STRAINER VENT | 01-1.5"-BFW1030-1HAC2A-1.0 "EOH | 1.5" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1073 | PD-061A
01-VBFW412 | STRAINER VENT | 01-1.5"-BFW1030-1HAC2A-1.0 "EOH | 1.5" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1074 | PD-061A
01-VBFW415 | DRAIN VALVE | 01-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1075 | PD-061A
01-VBFW416 | VENT VALVE | 01-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1076 | PD-062A
01-VBFW417 | VENT VALVE | 01-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1077 | PD-062A
01-VBFW422 | DRAIN VALVE | 01-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1078 | PD-061A
01-VBFW423 | DRAIN VALVE | 01-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1079 | PD-061A
01-VBFW424 | INSTRUMENT ISOLATION | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1080 | PD-062A
01-VBFW425 | VENT VALVE | 01-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1081 | PD-061A
01-VBFW426 | VENT VALVE | 01-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1082 | PD-061A
01-VBFW427 | STRAINER VENT | 01-1.5"-BFW1054-1HAC2A-1.0 "EOH | 1.5" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1083 | PD-061A
01-VBFW428 | STRAINER VENT | 01-1.5"-BFW1054-1HAC2A-1.0 "EOH | 1.5" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1084 | PD-061A
01-VBFW429 | BFW SUCTION LP DRUM SUPPLY CHECK | 01-12"-BFW1019-1DAA1A-1.0 "EOH | 12" | Check valve | BFW | 1DAA1A | Water | CL600 | BE | BE | 300 | 360 | S-STD | 1.0 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 2910 GPM, MIN FLOW- 840 GPM | 1085 | PD-060A
01-VBFW430 | VENT VALVE | 01-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 1086 | PD-060A
01-VBFW431 | INSTRUMENT ISOLATION | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1087 | PD-124A
01-VBFW432 | INSTRUMENT ISOLATION | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1088 | PD-124A
01-VBFW433 | IP BFW TO CRH LETDOWN SPRAY ISOLATION | 01-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1089 | PD-124A
01-VBFW434 | IP BFW TO CRH LETDOWN SPRAY ISOLATION | 01-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1090 | PD-124A
01-VBFW435 | INSTRUMENT ISOLATION | 01-0.75"-BFW1078-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1091 | PD-063A
01-VBFW436 | DRAIN VALVE | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1092 | PD-124A
01-VBFW437 | DRAIN VALVE | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1093 | PD-124A
01-VBFW438 | INSTRUMENT ISOLATION | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1094 | PD-062A
01-VBFW439 | INSTRUMENT ISOLATION | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1095 | PD-064A
01-VBFW440 | STRAINER VENT | 01-0.75"-BFW1037-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1096 | PD-064A
01-VBFW441 | STRAINER VENT | 01-0.75"-BFW1037-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1097 | PD-064A
01-VBFW442 | INSTRUMENT ISOLATION | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1098 | PD-064A
01-VBFW443 | INSTRUMENT ISOLATION | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1099 | PD-064A
01-VBFW444 | INSTRUMENT ISOLATION | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1100 | PD-064A
01-VBFW445 | INSTRUMENT ISOLATION | 01-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1101 | PD-064A
01-VBFW447 | DRAIN VALVE | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1102 | PD-124A
01-VBFW448 | DRAIN VALVE | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1103 | PD-124A
01-VBFW449 | DRAIN VALVE | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1104 | PD-064A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1105 | P&ID
01-VBFW450 | DRAIN VALVE | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1106 | PD-064A
01-VBFW451 | DRAIN VALVE | 01-0.75"-BFW1156-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1107 | PD-124A
01-VBFW452 | DRAIN VALVE | 01-0.75"-BFW1156-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1108 | PD-124A
01-VBFW453 | DRAIN VALVE | 01-0.75"-BFW1383-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1109 | PD-124A
01-VBFW454 | DRAIN VALVE | 01-0.75"-BFW1383-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1110 | PD-124A
01-VBFW459 | VENT VALVE | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1111 | PD-064A
01-VBFW460 | VENT VALVE | 01-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1112 | PD-064A
01-VBFW461 | DRAIN VALVE | 01-0.75"-BFW1473-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1113 | PD-064A
01-VBFW462 | DRAIN VALVE | 01-0.75"-BFW1473-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1114 | PD-064A
01-VBFW503 | STRAINER DRAIN | 01-1"-BFW1012-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1115 | PD-020A
01-VBFW505 | HPS TA SPRAY SUPPLY ISOLATION | 01-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1116 | PD-020A
01-VBFW506 | VENT VALVE | 01-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 1117 | PD-060A
01-VBFW509 | STRAINER DRAIN | 01-1"-BFW1001-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1118 | PD-020A
01-VBFW513 | HPS BYPASS SPRAY SUPPLY ISOLATION | 01-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1119 | PD-020A
01-VBFW519 | INSTRUMENT ISOLATION | 01-0.5"-BFW1035-1FAC1A-1.0 "EOH | 0.5" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1120 | PD-020A
01-VBFW521 | HPS TA SPRAY STRAINER ISOLATION | 01-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1121 | PD-020A
01-VBFW523 | HPS TA SPRAY STRAINER ISOLATION | 01-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1122 | PD-020A
01-VBFW525 | HPS TA SPRAY STRAINER ISOLATION | 01-3"-BFW1153-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1123 | PD-020A
01-VBFW529 | DRAIN VALVE | 01-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1124 | PD-020A
01-VBFW531 | HPS TA SPRAY SUPPLY ISOLATION | 01-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1125 | PD-020A
01-VBFW532 | STRAINER VENT | 01-0.75"-BFW1086-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1126 | PD-063A
01-VBFW539 | HPS BYPASS SPRAY SUPPLY CHECK | 01-3"-BFW1145-1FBB1A-1.5 "EOH | 3" | Check valve | BFW | 1FBB1A | Water | CL900 | BE | BE | 1400 | 500 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | TILTING DISC; MAX FLOW 350 GPM, MIN FLOW 80 GPM | 1127 | PD-020A
01-VBFW545 | DRAIN VALVE | 01-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1128 | PD-020A
01-VBFW547 | DRAIN VALVE | 01-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1129 | PD-020A
01-VBFW549 | HPS TA SPRAY STRAINER ISOLATION | 01-3"-BFW1153-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1130 | PD-020A
01-VBFW551 | DRAIN VALVE | 01-0.75"-BFW1145-1FBB1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FBB1A | Water | CL1500 | SWE | SWE | 1400 | 500 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1131 | PD-020A
01-VBFW553 | DRAIN VALVE | 01-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1132 | PD-020A
01-VBFW555 | HPS TA SPRAY STRAINER ISOLATION | 01-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1133 | PD-020A
01-VBFW557 | DRAIN VALVE | 01-0.75"-BFW1145-1FBB1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FBB1A | Water | CL1500 | SWE | SWE | 1400 | 500 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1134 | PD-020A
01-VBFW567 | VENT VALVE | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1135 | PD-020A
01-VBFW569 | VENT VALVE | 01-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1136 | PD-020A
01-VBFW570 | ISOLATION TO CRH LETDOWN ATTEMPERATORS | 01-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1137 | PD-124A
01-VBFW571 | ISOLATION TO CRH LETDOWN ATTEMPERATORS | 01-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1138 | PD-124A
01-VBFW572 | DRAIN VALVE | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1139 | PD-124A
01-VBFW573 | DRAIN VALVE | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1140 | PD-124A
01-VBFW574 | ISOLATION TO HRH TA SPRAY | 01-3"-BFW1108-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 1141 | PD-062A
01-VBFW575 | ISOLATION TO HRH TA SPRAY | 01-3"-BFW1108-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 1142 | PD-062A
01-VBFW576 | DRAIN VALVE | 01-0.75"-BFW1108-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1143 | PD-062A
01-VBFW577 | DRAIN VALVE | 01-0.75"-BFW1108-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1144 | PD-062A
01-VBFW578 | VENT VALVE | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1145 | PD-064A
01-VBFW579 | VENT VALVE | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1146 | PD-064A
01-VBFW600 | VENT VALVE | 01-0.75"-BFW1002-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1147 | PD-064A
01-VBFW601 | VENT VALVE | 01-0.75"-BFW1002-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1148 | PD-064A
01-VBFW602 | DRAIN VALVE | 01-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1149 | PD-064A
01-VBFW603 | DRAIN VALVE | 01-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1150 | PD-064A
01-VBFW604 | VENT VALVE | 01-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1151 | PD-061A
01-VBFW605 | VENT VALVE | 01-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1152 | PD-061A
01-VBFW606 | VENT VALVE | 01-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1153 | PD-061A
01-VBFW607 | VENT VALVE | 01-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1154 | PD-061A
01-VBFW608 | VENT VALVE | 01-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1155 | PD-061A
01-VBFW609 | VENT VALVE | 01-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1156 | PD-061A
01-VBFW610 | DRAIN VALVE | 01-0.75"-BFW1040-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1157 | PD-063A
01-VBFW611 | DRAIN VALVE | 01-0.75"-BFW1040-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1158 | PD-063A
01-VBFW612 | VENT VALVE | 01-0.75"-BFW1149-1HBD1A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HBD1A | Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H |  | 1159 | PD-020A
01-VBFW613 | VENT VALVE | 01-0.75"-BFW1149-1HBD1A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HBD1A | Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H |  | 1160 | PD-020A
01-VBFW614 | VENT VALVE | 01-0.75"-BFW1321-1HAC2A-2.0 "EIC | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 2.0 " | No | 94.03.68.150.02.3H |  | 1161 | PD-063A
01-VBFW615 | VENT VALVE | 01-0.75"-BFW1321-1HAC2A-2.0 "EIC | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 2.0 " | No | 94.03.68.150.02.3H |  | 1162 | PD-063A
01-VBFW616 | DRAIN VALVE | 01-0.75"-BFW1057-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1163 | PD-064A
01-VBFW617 | DRAIN VALVE | 01-0.75"-BFW1057-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1164 | PD-064A
01-VBFW618 | VENT VALVE | 01-0.75"-BFW1009-1FBD1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FBD1A | Water | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1165 | PD-034A
01-VBFW619 | VENT VALVE | 01-0.75"-BFW1009-1FBD1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FBD1A | Water | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1166 | PD-034A
01-VBFW622 | VENT VALVE | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1167 | PD-124A
01-VBFW623 | VENT VALVE | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1168 | PD-124A
01-VBFW624 | VENT VALVE | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1169 | PD-124A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1170 | P&ID
01-VBFW625 | VENT VALVE | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1171 | PD-124A
01-VBFW626 | DRAIN VALVE | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1172 | PD-124A
01-VBFW627 | DRAIN VALVE | 01-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1173 | PD-124A
01-VBFW628 | DRAIN VALVE | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1174 | PD-124A
01-VBFW629 | DRAIN VALVE | 01-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1175 | PD-124A
01-VBFW630 | INSTRUMENT | 01-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2 |  | 1176 | PD-064A
01-VBFW631 | INSTRUMENT ISOLATION | 01-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2 |  | 1177 | PD-064A
01-VBFW700 | INSTRUMENT ISOLATION | 01-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1178 | PD-063A
01-VBFW701 | INSTRUMENT ISOLATION | 01-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1179 | PD-063A
01-VBFW922 | CTA COOLER BFW OUTLET RECIRC CV ISOLATION | 01-6"-BFW1322-1HAC2A-2.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, EXTERNAL BONNET DRAIN | 1180 | PD-063A
01-VBFW923 | STRAINER VENT | 01-0.75"-BFW1086-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1181 | PD-063A
01-VBFW924 | INSTRUMENT ISOLATION | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1182 | PD-063A
01-VBFW925 | INSTRUMENT ISOLATION | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1183 | PD-063A
01-VBFW926 | INSTRUMENT ISOLATION | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1184 | PD-063A
01-VBFW927 | INSTRUMENT ISOLATION | 01-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1185 | PD-063A
01-VBFW928 | INSTRUMENT ISOLATION | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1186 | PD-063A
01-VBFW929 | INSTRUMENT ISOLATION | 01-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 1187 | PD-063A
01-VBFW933 | INSTRUMENT ISOLATION | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1188 | PD-064A
01-VBFW934 | INSTRUMENT ISOLATION | 01-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1189 | PD-064A
01-VBFW935 | INSTRUMENT ISOLATION | 01-0.75"-BFW1473-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1190 | PD-064A
01-VBFW936 | INSTRUMENT ISOLATION | 01-0.75"-BFW1473-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1191 | PD-064A
01-VCCF104 | UNIT 1 ENCLOSURE CONTAINMENT DRAIN ISOLATION VALVE | 01-2"-CCF1004-1BAA2A-1.0 "MOH | 2" | Ball valve | CCF | 1BAA2A | 19% Aqueous Ammonia and | CL600 | FTE | FTE | 0 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1192 | PD-520A
01-VCCF105 | UNIT 1 CONDENSATE AMMONIA FEED ISOLATION VALVE | 01-0.375"-CCF1030-1LCR1A-1.0 "MOH | 0.375" | Ball valve | CCF | 1LCR1A | 19% Aqueous Ammonia | CL900 | CTE | CTE | 790 | 115 | 0.065" Avg. Wall | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1193 | PD-053A
01-VCCW100 | INSTRUMENTATION | 01-0.75"-CCW1128-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1194 | PD-271A
01-VCCW101 | INSTRUMENTATION | 01-0.75"-CCW1105-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1195 | PD-271A
01-VCCW102 | HEAD TANK TO PUMP SUCTION ISOLATION | 01-2"-CCW1029-1BCA3A-1.0 "MOH | 2" | Ball valve | CCW | 1BCA3A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1196 | PD-270A
01-VCCW103 | CCW HEAD TANK DRAIN | 01-2"-CCW1051-1BCA3A-1.0 "MOH | 2" | Gate valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1197 | PD-270A
01-VCCW104 | INSTRUMENTATION | 01-0.75"-CCW1006-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1198 | PD-270A
01-VCCW105 | ACHE OUTLET ISOLATION/THROTTLING | 01-12"-CCW1105-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 1199 | PD-271A
01-VCCW106 | PUMP SUCTION ISOLATION | 01-24"-CCW1006-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 1200 | PD-270A
01-VCCW107 | PUMP DISCHARGE ISOLATION | 01-24"-CCW1023-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 1201 | PD-270A
01-VCCW108 | ACHE OUTLET ISOLATION/THROTTLING | 01-12"-CCW1108-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 1202 | PD-271A
01-VCCW109 | PUMP DISCHARGE ISOLATION | 01-24"-CCW1008-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 1203 | PD-270A
01-VCCW110 | VENT | 01-0.75"-CCW1111-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1204 | PD-271A
01-VCCW111 | VENT | 01-0.75"-CCW1045-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1205 | PD-270A
01-VCCW112 | VENT | 01-0.75"-CCW1046-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1206 | PD-270A
01-VCCW113 | DRAIN | 01-0.75"-CCW1023-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1207 | PD-270A
01-VCCW114 | POT FEEDER INLET ISOLATION | 01-2"-CCW1043-1BAB2A | 2" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1208 | PD-270A
01-VCCW115 | INSTRUMENTATION | 01-0.75"-CCW1006-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1209 | PD-270A
01-VCCW116 | INSTRUMENTATION | 01-0.75"-CCW1205-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1210 | PD-272A
01-VCCW117 | DRAIN | 01-0.75"-CCW1049-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1211 | PD-270A
01-VCCW118 | PUMP DISCHARGE CHECK | 01-24"-CCW1008-1BAB2A | 24" | Check valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | WAFER | WAFER | 150 | 150 | S-20 |  | No | 94.03.68.150.03.0 | DUAL PLATE, MAX FLOW - 12200 GPM, MIN FLOW - 7000 GPM | 1212 | PD-270A
01-VCCW119 | INSTRUMENTATION | 01-0.75"-CCW1006-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1213 | PD-270A
01-VCCW120 | ACHE INLET ISOLATION | 01-12"-CCW1120-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1214 | PD-271A
01-VCCW121 | PUMP SUCTION ISOLATION | 01-24"-CCW1015-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 1215 | PD-270A
01-VCCW122 | INSTRUMENTATION | 01-0.75"-CCW1015-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1216 | PD-270A
01-VCCW123 | ACHE INLET ISOLATION | 01-12"-CCW1123-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1217 | PD-271A
01-VCCW124 | VENT | 01-0.75"-CCW1113-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1218 | PD-271A
01-VCCW125 | ACHE OUTLET ISOLATION/THROTTLING | 01-12"-CCW1128-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 1219 | PD-271A
01-VCCW126 | BYPASS FOR ACHE BYPASS CV | 01-24"-CCW1127-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.04.2 | THROTTLING SERVICE | 1220 | PD-270A
01-VCCW127 | PUMP DISCHARGE CHECK | 01-24"-CCW1023-1BAB2A | 24" | Check valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | WAFER | WAFER | 150 | 150 | S-20 |  | No | 94.03.68.150.03.0 | DUAL PLATE, MAX FLOW - 12200 GPM, MIN FLOW - 7000 GPM | 1221 | PD-270A
01-VCCW128 | INSTRUMENTATION | 01-0.75"-CCW1001-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1222 | PD-275A
01-VCCW129 | ACHE INLET HEADER ISOLATION | 01-24"-CCW1129-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 1223 | PD-271A
01-VCCW130 | INSTRUMENTATION | 01-2"-CCW1030-1BCA3A-1.0 "MOH | 2" | Globe valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1224 | PD-270A
01-VCCW131 | INSTRUMENTATION | 01-0.75"-CCW1023-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1225 | PD-270A
01-VCCW132 | DRAIN | 01-2"-CCW1026-1BAB2A | 2" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1226 | PD-270A
01-VCCW133 | POT FEEDER OUTLET ISOLATION/THROTTLING | 01-2"-CCW1044-1BAB2A | 2" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 1227 | PD-270A
01-VCCW134 | DRAIN | 01-0.75"-CCW1008-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1228 | PD-270A
01-VCCW135 | INSTRUMENTATION | 01-0.75"-CCW1008-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1229 | PD-270A
01-VCCW136 | VENT | 01-0.75"-CCW1008-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1230 | PD-270A
01-VCCW137 | INSTRUMENTATION | 01-0.75"-CCW1015-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1231 | PD-270A
01-VCCW138 | INSTRUMENTATION | 01-0.75"-CCW1015-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1232 | PD-270A
01-VCCW139 | DRAIN | 01-0.75"-CCW1027-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1233 | PD-270A
01-VCCW140 | DRAIN | 01-0.75"-CCW1141-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1234 | PD-270A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1235 | P&ID
01-VCCW141 | DRAIN | 01-0.75"-CCW1050-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1236 | PD-270A
01-VCCW142 | POT FEEDER OUTLET ISOLATION/THROTTLING | 01-0.75"-CCW1044-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 1237 | PD-270A
01-VCCW143 | VENT | 01-0.75"-CCW1115-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1238 | PD-271A
01-VCCW144 | ACHE INLET ISOLATION | 01-12"-CCW1142-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1239 | PD-271A
01-VCCW145 | ACHE INLET ISOLATION | 01-12"-CCW1145-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1240 | PD-271A
01-VCCW146 | VENT | 01-0.75"-CCW1114-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1241 | PD-271A
01-VCCW147 | VENT | 01-0.75"-CCW1012-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 1242 | PD-275A
01-VCCW148 | ACHE BYPASS CV ISOLATION | 01-24"-CCW1141-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 1243 | PD-270A
01-VCCW149 | ACHE BYPASS CV ISOLATION | 01-24"-CCW1141-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 1244 | PD-270A
01-VCCW150 | VENT | 01-0.75"-CCW1112-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1245 | PD-271A
01-VCCW151 | DRAIN | 01-0.75"-CCW1042-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1246 | PD-270A
01-VCCW152 | DRAIN | 01-2"-CCW1022-1BAB2A | 2" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1247 | PD-270A
01-VCCW153 | SYSTEM BALANCING CV ISOLATION | 01-16"-CCW1141-1BAB2A | 16" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1248 | PD-270A
01-VCCW154 | SYSTEM BALANCING CV ISOLATION | 01-16"-CCW1141-1BAB2A | 16" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1249 | PD-270A
01-VCCW155 | SYSTEM BALANCING CV BYPASS | 01-10"-CCW1013-1BAB2A | 10" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.2H | THROTTLING SERVICE | 1250 | PD-270A
01-VCCW156 | DRAIN | 01-0.75"-CCW1141-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1251 | PD-270A
01-VCCW157 | INSTRUMENTATION | 01-0.75"-CCW1167-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1252 | PD-271A
01-VCCW158 | VENT | 01-0.75"-CCW1009-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 1253 | PD-270A
01-VCCW159 | VENT | 01-0.75"-CCW1019-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 1254 | PD-270A
01-VCCW160 | ACHE INLET ISOLATION | 01-12"-CCW1160-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1255 | PD-271A
01-VCCW161 | VENT | 01-0.75"-CCW1031-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1256 | PD-275A
01-VCCW162 | INSTRUMENTATION | 01-0.75"-CCW1031-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1257 | PD-275A
01-VCCW163 | INSTRUMENTATION | 01-0.75"-CCW1014-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1258 | PD-275A
01-VCCW164 | VENT | 01-0.75"-CCW1205-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.2H |  | 1259 | PD-272A
01-VCCW165 | DRAIN | 01-0.75"-CCW1012-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1260 | PD-275A
01-VCCW166 | INSTRUMENTATION | 01-0.75"-CCW1021-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1261 | PD-275A
01-VCCW167 | ACHE OUTLET ISOLATION/THROTTLING | 01-12"-CCW1167-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 1262 | PD-271A
01-VCCW168 | DRAIN | 01-0.75"-CCW1229-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1263 | PD-272A
01-VCCW169 | INSTRUMENTATION | 01-0.75"-CCW1012-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1264 | PD-275A
01-VCCW170 | ACHE OUTLET ISOLATION/THROTTLING | 01-12"-CCW1170-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 1265 | PD-271A
01-VCCW171 | INSTRUMENTATION | 01-0.75"-CCW1125-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1266 | PD-271A
01-VCCW172 | BFP SUPPLY ISOLATION | 01-3"-CCW1205-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 1267 | PD-272A
01-VCCW173 | INSTRUMENTATION | 01-0.75"-CCW1206-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1268 | PD-272A
01-VCCW174 | INSTRUMENTATION | 01-0.75"-CCW1108-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1269 | PD-271A
01-VCCW175 | SAMPLE PANEL FLOW THROTTLING | 01-4"-CCW1206-1BAB2A | 4" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 1270 | PD-272A
01-VCCW176 | VENT | 01-0.75"-CCW1225-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1271 | PD-272A
01-VCCW177 | BFP SUPPLY ISOLATION | 01-3"-CCW1211-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 1272 | PD-272A
01-VCCW178 | DRAIN | 01-0.75"-CCW1211-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1273 | PD-272A
01-VCCW179 | INSTRUMENTATION | 01-0.75"-CCW1226-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1274 | PD-272A
01-VCCW180 | INSTRUMENTATION | 01-0.75"-CCW1225-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1275 | PD-272A
01-VCCW181 | BFP FLOW THROTTLING | 01-3"-CCW1226-1BAB2A | 3" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 1276 | PD-272A
01-VCCW182 | BFP FLOW THROTTLING | 01-3"-CCW1225-1BAB2A | 3" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 1277 | PD-272A
01-VCCW183 | SAMPLE PANEL SUPPLY ISOLATION | 01-4"-CCW1229-1BAB2A | 4" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1278 | PD-272A
01-VCCW184 | VENT | 01-0.75"-CCW1206-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1279 | PD-272A
01-VCCW185 | TCU RETURN ISOLATION | 01-3"-CCW1010-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 1280 | PD-272A
01-VCCW186 | TCU SUPPLY ISOLATION | 01-3"-CCW1011-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 1281 | PD-272A
01-VCCW187 | INSTRUMENTATION | 01-0.75"-CCW1229-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1282 | PD-272A
01-VCCW188 | DRAIN | 01-0.75"-CCW1205-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1283 | PD-272A
01-VCCW189 | VENT | 01-0.75"-CCW1226-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1284 | PD-272A
01-VCCW190 | INSTRUMENTATION | 01-2"-CCW1017-1BCA3A-1.0 "MOH | 2" | Globe valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1285 | PD-270A
01-VCCW191 | INSTRUMENTATION | 01-2"-CCW1061-1BCA3A-1.0 "MOH | 2" | Globe valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1286 | PD-270A
01-VCCW192 | VENT | 01-0.75"-CCW1141-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 1287 | PD-270A
01-VCCW193 | VENT | 01-0.75"-CCW1141-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 1288 | PD-270A
01-VCCW194 | VENT | 01-0.75"-CCW1211-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.2H |  | 1289 | PD-272A
01-VCCW195 | DRAIN | 01-0.75"-CCW1031-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1290 | PD-275A
01-VCCW196 | DRAIN | 01-0.75"-CCW1000-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1291 | PD-270A
01-VCCW200 | VENT | 01-0.75"-CCW1101-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1292 | PD-270A
01-VCCW201 | VENT | 01-0.75"-CCW1103-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1293 | PD-270A
01-VCCW211 | INSTRUMENTATION | 01-0.75"-CCW1076-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1294 | PD-274A
01-VCCW212 | INSTRUMENTATION | 01-0.75"-CCW1032-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1295 | PD-274A
01-VCCW213 | INSTRUMENTATION | 01-0.75"-CCW1077-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1296 | PD-274A
01-VCCW214 | INSTRUMENTATION | 01-0.75"-CCW1078-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1297 | PD-274A
01-VCCW215 | INSTRUMENTATION | 01-0.75"-CCW1079-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1298 | PD-274A
01-VCCW216 | DRAIN | 01-0.75"-CCW1128-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1299 | PD-271A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1300 | P&ID
01-VCCW217 | DRAIN | 01-0.75"-CCW1105-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1301 | PD-271A
01-VCCW218 | DRAIN | 01-0.75"-CCW1167-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1302 | PD-271A
01-VCCW219 | DRAIN | 01-0.75"-CCW1108-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1303 | PD-271A
01-VCCW220 | DRAIN | 01-0.75"-CCW1170-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1304 | PD-271A
01-VCCW221 | INSTRUMENTATION | 01-0.75"-CCW1075-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1305 | PD-274A
01-VCCW222 | INSTRUMENTATION | 01-0.75"-CCW1072-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1306 | PD-274A
01-VCCW224 | INSTRUMENTATION | 01-0.75"-CCW1073-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1307 | PD-274A
01-VCCW225 | INSTRUMENTATION | 01-0.75"-CCW1074-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1308 | PD-274A
01-VCCW226 | DRAIN | 01-0.75"-CCW1142-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1309 | PD-271A
01-VCCW227 | DRAIN | 01-0.75"-CCW1145-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1310 | PD-271A
01-VCCW228 | DRAIN | 01-0.75"-CCW1123-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1311 | PD-271A
01-VCCW229 | DRAIN | 01-0.75"-CCW1160-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1312 | PD-271A
01-VCCW230 | DRAIN | 01-0.75"-CCW1120-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1313 | PD-271A
01-VCCW300 | INSTRUMENTATION | 01-0.75"-CCW1170-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1314 | PD-271A
01-VCCW301 | VENT | 01-0.75"-CCW1325-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.3H |  | 1315 | PD-273A
01-VCCW302 | VENT | 01-0.75"-CCW1332-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.3H |  | 1316 | PD-273A
01-VCCW304 | LUBE OIL MODULE SUPPLY ISOLATION | 01-14"-CCW1332-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1317 | PD-273A
01-VCCW305 | LUBE OIL MODULE OUTLET ISOLATION/THROTTLING | 01-14"-CCW1305-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 1318 | PD-273A
01-VCCW306 | GLYCOL FILL CHECK | 01-2"-CCW1028-1BCA3A-1.0 "MOH | 2" | Check valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 | PISTON | 1319 | PD-270A
01-VCCW307 | INSTRUMENTATION | 01-0.75"-CCW1020-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1320 | PD-273A
01-VCCW308 | DRAIN | 01-0.75"-CCW1020-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1321 | PD-273A
01-VCCW318 | DRAIN | 01-0.75"-CCW1334-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1322 | PD-274A
01-VCCW319 | DRAIN | 01-0.75"-CCW1335-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1323 | PD-274A
01-VCCW320 | GENERATOR COOLER SUPPLY ISOLATION | 01-6"-CCW1039-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1324 | PD-274A
01-VCCW321 | INSTRUMENTATION | 01-0.75"-CCW1039-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1325 | PD-274A
01-VCCW322 | DRAIN | 01-0.75"-CCW1305-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1326 | PD-273A
01-VCCW323 | INSTRUMENTATION | 01-0.75"-CCW1305-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1327 | PD-273A
01-VCCW324 | DRAIN | 01-0.75"-CCW1332-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1328 | PD-273A
01-VCCW325 | LUBE OIL MODULE SUPPLY ISOLATION | 01-14"-CCW1325-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1329 | PD-273A
01-VCCW326 | DRAIN | 01-0.75"-CCW1325-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1330 | PD-273A
01-VCCW327 | INSTRUMENTATION | 01-0.75"-CCW1325-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.2H |  | 1331 | PD-273A
01-VCCW328 | VENT | 01-0.75"-CCW1325-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1332 | PD-273A
01-VCCW329 | INSTRUMENTATION | 01-0.75"-CCW1332-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1333 | PD-273A
01-VCCW330 | GENERATOR COOLER SUPPLY ISOLATION | 01-6"-CCW1038-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1334 | PD-274A
01-VCCW331 | INSTRUMENTATION | 01-0.75"-CCW1142-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1335 | PD-271A
01-VCCW332 | GENERATOR COOLER SUPPLY ISOLATION | 01-6"-CCW1037-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1336 | PD-274A
01-VCCW333 | INSTRUMENTATION | 01-0.75"-CCW1145-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1337 | PD-271A
01-VCCW334 | GENERATOR COOLER SUPPLY ISOLATION | 01-6"-CCW1036-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1338 | PD-274A
01-VCCW335 | INSTRUMENTATION | 01-0.75"-CCW1123-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1339 | PD-271A
01-VCCW336 | GENERATOR COOLER SUPPLY ISOLATION | 01-6"-CCW1035-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1340 | PD-274A
01-VCCW337 | INSTRUMENTATION | 01-0.75"-CCW1160-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1341 | PD-271A
01-VCCW338 | GENERATOR COOLER SUPPLY ISOLATION | 01-6"-CCW1034-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1342 | PD-274A
01-VCCW339 | INSTRUMENTATION | 01-0.75"-CCW1120-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1343 | PD-271A
01-VCCW340 | VENT | 01-0.75"-CCW1332-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1344 | PD-273A
01-VCCW341 | LUBE OIL MODULE OUTLET ISOLATION/THROTTLING | 01-14"-CCW1020-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 1345 | PD-273A
01-VCCW342 | GENERATOR COOLER SUPPLY ISOLATION | 01-6"-CCW1033-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1346 | PD-274A
01-VCCW343 | INSTRUMENTATION | 01-0.75"-CCW1033-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1347 | PD-274A
01-VCCW344 | GENERATOR COOLER SUPPLY ISOLATION | 01-6"-CCW1032-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 1348 | PD-274A
01-VCCW345 | GLYCOL FILL ISOLATION | 01-2"-CCW1028-1BCA3A-1.0 "MOH | 2" | Ball valve | CCW | 1BCA3A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1349 | PD-270A
01-VCCW346 | ECA COMPRESSOR RETURN ISOLATION | 01-3"-CCW1007-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 1350 | PD-275A
01-VCCW347 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 01-6"-CCW1079-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 1351 | PD-274A
01-VCCW348 | DRAIN | 01-0.75"-CCW1336-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1352 | PD-274A
01-VCCW349 | GENERATOR COOLER RETURN HEADER ISOLATION/THROTTLING | 01-14"-CCW1132-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 1353 | PD-274A
01-VCCW350 | INSTRUMENTATION | 01-0.75"-CCW1038-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1354 | PD-274A
01-VCCW351 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 01-6"-CCW1078-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 1355 | PD-274A
01-VCCW352 | INSTRUMENTATION | 01-0.75"-CCW1037-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1356 | PD-274A
01-VCCW353 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 01-6"-CCW1077-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 1357 | PD-274A
01-VCCW354 | INSTRUMENTATION | 01-0.75"-CCW1036-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1358 | PD-274A
01-VCCW355 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 01-6"-CCW1076-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 1359 | PD-274A
01-VCCW356 | INSTRUMENTATION | 01-0.75"-CCW1035-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1360 | PD-274A
01-VCCW357 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 01-6"-CCW1075-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 1361 | PD-274A
01-VCCW358 | INSTRUMENTATION | 01-0.75"-CCW1034-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1362 | PD-274A
01-VCCW359 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 01-6"-CCW1074-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 1363 | PD-274A
01-VCCW360 | INSTRUMENTATION | 01-0.75"-CCW1007-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1364 | PD-275A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1365 | P&ID
01-VCCW361 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 01-6"-CCW1073-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 1366 | PD-274A
01-VCCW362 | ECA COMPRESSOR SUPPLY ISOLATION | 01-3"-CCW1021-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 1367 | PD-275A
01-VCCW363 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 01-6"-CCW1072-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 1368 | PD-274A
01-VCCW364 | GENERATOR COOLER SUPPLY HEADER ISOLATION | 01-14"-CCW1662-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 1369 | PD-274A
01-VCCW365 | VENT | 01-0.75"-CCW1023-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1370 | PD-270A
01-VCCW366 | ACHE OUTLET HEADER ISOLATION | 01-24"-CCW1125-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 135 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 1371 | PD-271A
01-VCCW367 | INSTRUMENTATION | 01-0.75"-CCW1044-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1372 | PD-270A
01-VCCW368 | INSTRUMENTATION | 01-0.75"-CCW1043-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1373 | PD-270A
01-VCCW369 | ECA COMPRESSOR FLOW THROTTLING | 01-3"-CCW1007-1BAB2A | 3" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 1374 | PD-275A
01-VCCW370 | ECA COMPRESSOR RETURN ISOLATION | 01-3"-CCW1014-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 1375 | PD-275A
01-VCCW371 | DRAIN | 01-0.75"-CCW1337-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1376 | PD-274A
01-VCCW372 | DRAIN | 01-0.75"-CCW1052-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1377 | PD-274A
01-VCCW373 | DRAIN | 01-0.75"-CCW1053-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1378 | PD-274A
01-VCCW374 | DRAIN | 01-0.75"-CCW1054-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1379 | PD-274A
01-VCCW375 | DRAIN | 01-0.75"-CCW1055-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1380 | PD-274A
01-VCCW376 | DRAIN | 01-0.75"-CCW1056-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1381 | PD-274A
01-VCCW377 | DRAIN | 01-0.75"-CCW1057-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1382 | PD-274A
01-VCCW378 | DRAIN | 01-0.75"-CCW1058-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1383 | PD-274A
01-VCCW379 | DRAIN | 01-0.75"-CCW1059-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1384 | PD-274A
01-VCCW380 | ECA COMPRESSOR SUPPLY ISOLATION | 01-3"-CCW1001-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 1385 | PD-275A
01-VCCW381 | ECA COMPRESSOR FLOW THROTTLING | 01-3"-CCW1014-1BAB2A | 3" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 1386 | PD-275A
01-VCCW382 | VENT | 01-0.75"-CCW1062-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1387 | PD-274A
01-VCCW383 | VENT | 01-0.75"-CCW1063-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1388 | PD-274A
01-VCCW384 | VENT | 01-0.75"-CCW1064-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1389 | PD-274A
01-VCCW385 | VENT | 01-0.75"-CCW1065-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1390 | PD-274A
01-VCCW386 | VENT | 01-0.75"-CCW1066-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1391 | PD-274A
01-VCCW387 | VENT | 01-0.75"-CCW1067-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1392 | PD-274A
01-VCCW388 | VENT | 01-0.75"-CCW1068-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1393 | PD-274A
01-VCCW389 | VENT | 01-0.75"-CCW1069-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1394 | PD-274A
01-VCCW391 | VENT | 01-0.75"-CCW1001-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1395 | PD-275A
01-VCCW392 | DRAIN | 01-0.75"-CCW1014-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1396 | PD-275A
01-VCCW393 | DRAIN | 01-0.75"-CCW1007-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1397 | PD-275A
01-VCCW396 | VENT | 01-0.75"-CCW1021-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1398 | PD-275A
01-VCCW398 | DRAIN | 01-0.75"-CCW1333-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1399 | PD-274A
01-VCCW399 | DRAIN | 01-0.75"-CCW1338-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1400 | PD-274A
01-VCCW400 | DRAIN | 01-0.75"-CCW1339-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1401 | PD-274A
01-VCCW401 | DRAIN | 01-0.75"-CCW1340-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1402 | PD-274A
01-VCCW402 | DRAIN | 01-0.75"-CCW1341-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1403 | PD-274A
01-VCCW403 | DRAIN | 01-0.75"-CCW1342-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1404 | PD-274A
01-VCCW404 | DRAIN | 01-0.75"-CCW1343-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1405 | PD-274A
01-VCCW405 | DRAIN | 01-0.75"-CCW1344-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1406 | PD-274A
01-VCCW406 | DRAIN | 01-0.75"-CCW1345-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1407 | PD-274A
01-VCCW407 | DRAIN | 01-0.75"-CCW1346-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1408 | PD-274A
01-VCCW408 | DRAIN | 01-0.75"-CCW1347-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1409 | PD-274A
01-VCCW409 | DRAIN | 01-0.75"-CCW1348-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1410 | PD-274A
01-VCCW410 | VENT | 01-0.75"-CCW1662-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1411 | PD-274A
01-VCCW411 | VENT | 01-0.75"-CCW1132-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 1412 | PD-274A
01-VCCW412 | BFP RETURN ISOLATION | 01-3"-CCW1226-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 1413 | PD-272A
01-VCCW413 | BFP RETURN ISOLATION | 01-3"-CCW1225-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 1414 | PD-272A
01-VCCW414 | TCU FILL ISOLATION | 01-0.75"-CCW1133-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1415 | PD-272A
01-VCCW415 | SAMPLE PANEL RETURN ISOLATION | 01-4"-CCW1206-1BAB2A | 4" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 |  | 1416 | PD-272A
01-VCCW453 | INSTRUMENTATION | 01-0.75"-CCW1211-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 1417 | PD-272A
01-VCMG102 | INSTRUMENTATION | 01-0.75"-CMG1016-1BCB6A | 0.75" | Globe valve | CMG | 1BCB6A | CARBON DIOXIDE | CL800 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 1418 | PD-571
01-VCMG103 | H2 ISOLATION | 01-1.5"-CMG1013-1BAA2A | 1.5" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 1419 | PD-571
01-VCMG104 | INSTRUMENTATION | 01-0.75"-CMG1102-1BCA1A | 0.75" | Globe valve | CMG | 1BCA1A | NITROGEN | CL800 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 1420 | PD-570
01-VCMG113 | H2 ISOLATION | 01-1.5"-CMG1013-1BAA2A | 1.5" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 1421 | PD-571
01-VCMG119 | INSTRUMENTATION | 01-0.75"-CMG1101-1BCA1A | 0.75" | Globe valve | CMG | 1BCA1A | NITROGEN | CL800 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 1422 | PD-570
01-VCMG122 | INSTRUMENTATION | 01-0.75"-CMG1010-1BCB6A | 0.75" | Globe valve | CMG | 1BCB6A | CARBON DIOXIDE | CL800 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 1423 | PD-571
01-VCMG602 | VENT | 01-0.75"-CMG1013-1BAA2A | 0.75" | Globe valve | CMG | 1BAA2A | HYDROGEN | CL800 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 1424 | PD-571
01-VCMG604 | N2 PURGE CONNECTION | 01-0.75"-CMG1002-1BAA2A | 0.75" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 1425 | PD-571
01-VCND100 | STRAINER VENT VALVE | 01-0.5"-CND1074-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1426 | PD-051A
01-VCND101 | IRON FILTER DRAIN | 01-0.75"-CND1056-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1427 | PD-052A
01-VCND103 | CONDENSATE EMERGENCY DUMP CV ISOLATION | 01-6"-CND1103-1EAA2A-1.0 "MOH | 6" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1428 | PD-053A
01-VCND104 | INSTRUMENT ISOLATION | 01-0.75"-CND1027-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1429 | PD-051A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1430 | P&ID
01-VCND105 | DRAIN VALVE | 01-0.75"-CND1415-1EAA1A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 790 | 310 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1431 | PD-040A
01-VCND106 | VENT VALVE | 01-0.75"-CND1050-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1432 | PD-050A
01-VCND108 | DRAIN VALVE | 01-0.75"-CND1062-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1433 | PD-030A
01-VCND109 | CRH VENTILATOR SPRAY SUPPLY ISOLATION | 01-3"-CND1062-1EAA2A-1.0 "MIC | 3" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.2H | FLEXIBLE WEDGE | 1434 | PD-030A
01-VCND110 | VENT VALVE | 01-0.75"-CND1062-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1435 | PD-030A
01-VCND111 | CRH VENTILATOR SPRAY SUPPLY CHECK VALVE | 01-3"-CND1092-1EBB1A-1.0 "EOH | 3" | Check valve | CND | 1EBB1A | Water | CL600 | BE | BE | 790 | 380 | S-40 | 1.0 " | Yes | 94.03.68.150.01.2H | SWING CHECK; FLOW: 25 GPM (MIN), 160 GPM (MAX) | 1436 | PD-030A
01-VCND112 | INSTRUMENT ISOLATION | 01-0.75"-CND1060-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1437 | PD-051A
01-VCND113 | CND PUMP CAN VENT VALVE | 01-1"-CND1131-1BAA2A-1.0 "MOH | 1" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1438 | PD-051A
01-VCND114 | STRAINER DRAIN | 01-0.75"-CND1058-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1439 | PD-052A
01-VCND115 | LPS BYPASS SPRAY SUPPLY CHECK VALVE | 01-1.5"-CND1415-1EAA1A-1.0 "MOH | 1.5" | Check valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 790 | 310 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | PISTON CHECK; FLOW: 10 GPM (MIN), 40 GPM (MAX) | 1440 | PD-040A
01-VCND116 | DRAIN VALVE | 01-0.75"-CND1256-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1441 | PD-034A
01-VCND117 | CND PUMP DISCHARGE CHECK VALVE | 01-10"-CND1017-1EAA2A-1.0 "MOH | 10" | Check valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 500 GPM (MIN), 2000 GPM (MAX) | 1442 | PD-051A
01-VCND118 | STRAINER VENT VALVE | 01-0.5"-CND1074-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1443 | PD-051A
01-VCND119 | HRH BYPASS SPRAY SUPPLY ISOLATION | 01-6"-CND1256-1EAA2A-1.0 "MIC | 6" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1444 | PD-034A
01-VCND121 | HRH BYPASS SPRAY SUPPLY CHECK VALVE | 01-6"-CND1251-1EBB1A-1.5 "EOH | 6" | Check valve | CND | 1EBB1A | Water | CL600 | BE | BE | 790 | 380 | S-40 | 1.5 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 250 GPM (MIN), 850 GPM (MAX) | 1445 | PD-034A
01-VCND123 | INSTRUMENT ISOLATION | 01-0.75"-CND1002-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1446 | PD-052A
01-VCND124 | INSTRUMENT ISOLATION | 01-0.5"-CND1072-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1447 | PD-052A
01-VCND125 | INSTRUMENT ISOLATION | 01-0.5"-CND3317-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.2H |  | 1448 | PD-034A
01-VCND126 | ST HOOD SPRAY SUPPLY ISOLATION | 01-1.5"-CND1002-1EAA2A-1.0 "MIC | 1.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1449 | PD-052A
01-VCND127 | VENT VALVE | 01-0.75"-CND1027-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1450 | PD-051A
01-VCND128 | CND PUMP DISCHARGE ISOLATION | 01-10"-CND1027-1EAA2A-1.0 "MOH | 10" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1451 | PD-051A
01-VCND129 | STRAINER VENT VALVE | 01-0.5"-CND1075-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1452 | PD-051A
01-VCND130 | INSTRUMENT ISOLATION | 01-0.75"-CND1017-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1453 | PD-051A
01-VCND131 | INSTRUMENT ISOLATION | 01-0.75"-CND1071-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1454 | PD-051A
01-VCND132 | CONDENSATE RECIRC CV DOWNSTREAM ISOLATION | 01-8"-CND1033-1EBB1A-1.0 "MOH | 8" | Ball valve | CND | 1EBB1A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.150.08.0 | FULL BORE, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED, 12" OPERATOR MOUNTING KIT | 1455 | PD-053A
01-VCND133 | STRAINER VENT VALVE | 01-0.5"-CND1023-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1456 | PD-051A
01-VCND134 | CND TO ACC CURTAIN SPRAY FE ISOLATION | 01-4"-CND1038-1EAA2A-1.0 "MIC | 4" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1457 | PD-052A
01-VCND135 | STRAINER VENT VALVE | 01-0.5"-CND1075-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1458 | PD-051A
01-VCND136 | DRAIN VALVE | 01-0.75"-CND1072-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1459 | PD-052A
01-VCND137 | INSTRUMENT ISOLATION | 01-0.75"-CND1094-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1460 | PD-051A
01-VCND138 | VENT VALVE | 01-0.75"-CND1072-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1461 | PD-052A
01-VCND139 | INSTRUMENT ISOLATION | 01-0.75"-CND1051-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1462 | PD-052A
01-VCND140 | IRON FILTER VENT VALVE | 01-0.75"-CND1052-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1463 | PD-052A
01-VCND141 | LPS BYPASS SPRAY SUPPLY ISOLATION | 01-1.5"-CND1459-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1464 | PD-040A
01-VCND142 | INSTRUMENT ISOLATION | 01-0.75"-CND1021-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1465 | PD-051A
01-VCND143 | INSTRUMENT ISOLATION | 01-0.75"-CND1021-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1466 | PD-051A
01-VCND144 | IRON FILTER DRAIN VALVE | 01-0.75"-CND1044-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1467 | PD-052A
01-VCND145 | ST HOOD SPRAY VALVE ISOLATION | 01-1.5"-CND1002-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H | WEDGE GATE | 1468 | PD-052A
01-VCND146 | INSTRUMENT ISOLATION | 01-0.75"-CND1072-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1469 | PD-052A
01-VCND147 | ST HOOD SPRAY CV BYPASS VALVE | 01-1.5"-CND1043-1EAA2A-1.0 "MIC | 1.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1470 | PD-052A
01-VCND148 | CND PUMP DISCHARGE CHECK VALVE | 01-10"-CND1027-1EAA2A-1.0 "MOH | 10" | Check valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 500 GPM (MIN), 2000 GPM (MAX) | 1471 | PD-051A
01-VCND149 | VENT VALVE | 01-0.75"-CND1189-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1472 | PD-053A
01-VCND150 | CND DISCHARGE SAMPLE ISOLATION | 01-0.5"-CND1029-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1473 | PD-053A
01-VCND151 | INSTRUMENT ISOLATION | 01-0.75"-CND1027-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1474 | PD-052A
01-VCND152 | DRAIN VALVE | 01-0.75"-CND1033-1EBB1A-1.0 "MOH | 0.75" | Gate valve | CND | 1EBB1A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1475 | PD-053A
01-VCND153 | DRAIN VALVE | 01-0.75"-CND1103-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1476 | PD-053A
01-VCND154 | STRAINER VENT VALVE | 01-0.5"-CND1054-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1477 | PD-051A
01-VCND155 | CND DISCHARGE SAMPLE ISOLATION | 01-0.5"-CND1026-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1478 | PD-053A
01-VCND156 | INSTRUMENT ISOLATION | 01-0.5"-CND1869-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1479 | PD-040A
01-VCND157 | CND PUMP CAN VENT VALVE | 01-1"-CND1030-1BAA2A-1.0 "MOH | 1" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1480 | PD-051A
01-VCND158 | DRAIN VALVE | 01-0.75"-CND1459-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1481 | PD-040A
01-VCND159 | INSTRUMENT ISOLATION | 01-0.5"-CND1889-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1482 | PD-030A
01-VCND160 | CONDENSATE IRON FILTER BYPASS VALVE ISOLATION | 01-12"-CND1088-1EAA2A-1.0 "MOH | 12" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1483 | PD-052A
01-VCND162 | INSTRUMENT ISOLATION | 01-0.5"-CND1888-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1484 | PD-030A
01-VCND163 | CONDENSATE IRON FILTER BYPASS VALVE ISOLATION | 01-12"-CND1088-1EAA2A-1.0 "MOH | 12" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1485 | PD-052A
01-VCND164 | INSTRUMENT ISOLATION | 01-0.75"-CND1070-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1486 | PD-051A
01-VCND165 | STRAINER VENT VALVE | 01-0.5"-CND1076-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1487 | PD-051A
01-VCND166 | STRAINER DRAIN | 01-2"-CND1012-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE, TO BE RATED FOR VACUUM SERVICE | 1488 | PD-051A
01-VCND167 | DRAIN VALVE | 01-0.75"-CND1094-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1489 | PD-051A
01-VCND168 | STRAINER VENT | 01-0.5"-CND1076-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1490 | PD-051A
01-VCND169 | INSTRUMENT ISOLATION | 01-0.5"-CND1868-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1491 | PD-040A
01-VCND170 | INSTRUMENT ISOLATION | 01-0.5"-CND3321-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.2H |  | 1492 | PD-034A
01-VCND171 | STRAINER DRAIN VALVE | 01-2"-CND1067-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H | WEDGE GATE | 1493 | PD-051A
01-VCND172 | CONDENSATE IRON FILTER MANUAL ISOLATION | 01-12"-CND1001-1EAA2A-1.0 "MOH | 12" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1494 | PD-052A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1495 | P&ID
01-VCND173 | STRAINER DRAIN VALVE | 01-2"-CND1073-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE, TO BE RATED FOR VACUUM SERVICE | 1496 | PD-051A
01-VCND174 | CONDENSATE IRON FILTER MANUAL ISOLATION | 01-12"-CND1000-1EAA2A-1.0 "MOH | 12" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1497 | PD-052A
01-VCND175 | INSTRUMENT ISOLATION | 01-0.5"-CND1072-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1498 | PD-052A
01-VCND176 | STRAINER DRAIN | 01-2"-CND1068-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H | WEDGE GATE | 1499 | PD-051A
01-VCND177 | IRON FILTER VENT | 01-0.75"-CND1089-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1500 | PD-052A
01-VCND178 | STRAINER DRAIN VALVE | 01-2"-CND1069-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H | WEDGE GATE | 1501 | PD-051A
01-VCND179 | INSTRUMENT ISOLATION | 01-0.75"-CND1010-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1502 | PD-051A
01-VCND180 | INSTRUMENT ISOLATION | 01-0.75"-CND1079-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1503 | PD-052A
01-VCND181 | INSTRUMENT ISOLATION | 01-0.75"-CND1015-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1504 | PD-051A
01-VCND182 | VENT VALVE | 01-2"-CND1042-1EAA2A-1.0 "MOH | 2" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H | WEDGE GATE | 1505 | PD-052A
01-VCND183 | INSTRUMENT ISOLATION | 01-0.75"-CND1070-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1506 | PD-051A
01-VCND184 | INSTRUMENT ISOLATION | 01-0.75"-CND1087-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1507 | PD-052A
01-VCND185 | CND PUMP DISCHARGE CHECK VALVE | 01-10"-CND1094-1EAA2A-1.0 "MOH | 10" | Check valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 500 GPM (MIN), 2000 GPM (MAX) | 1508 | PD-051A
01-VCND186 | VENT VALVE | 01-0.75"-CND1002-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1509 | PD-052A
01-VCND187 | INSTRUMENT ISOLATION | 01-0.75"-CND1077-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1510 | PD-052A
01-VCND188 | DRAIN VALVE | 01-0.75"-CND1088-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1511 | PD-052A
01-VCND189 | DRAIN VALVE | 01-0.75"-CND1017-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1512 | PD-051A
01-VCND190 | INSTRUMENT ISOLATION | 01-0.5"-CND1072-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1513 | PD-052A
01-VCND191 | STRAINER VENT | 01-0.5"-CND1024-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1514 | PD-051A
01-VCND192 | INSTRUMENT ISOLATION | 01-0.75"-CND1071-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1515 | PD-051A
01-VCND193 | INSTRUMENT ISOLATION | 01-0.75"-CND1185-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1516 | PD-052A
01-VCND194 | CND PUMP DISCHARGE ISOLATION | 01-10"-CND1094-1EAA2A-1.0 "MOH | 10" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1517 | PD-051A
01-VCND195 | DRAIN VALVE | 01-0.75"-CND1098-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1518 | PD-053A
01-VCND196 | DRAIN VALVE | 01-0.75"-CND1027-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1519 | PD-051A
01-VCND197 | DRAIN VALVE | 01-0.75"-CND1259-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 1520 | PD-054A
01-VCND198 | HP DRAINS TANK QUENCH SPRAY VALVE ISOLATION | 01-3"-CND1202-1EAA2A-1.0 "MOH | 3" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1521 | PD-304A
01-VCND200 | DRAIN VALVE | 01-0.75"-CND1202-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1522 | PD-304A
01-VCND201 | GLAND STEAM DSH SPRAY SUPPLY STRAINER ISOLATION | 01-1"-CND1181-1EAA2A-1.0 "MIC | 1" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.01.1H | WEDGE GATE | 1523 | PD-300A
01-VCND207 | INSTRUMENT ISOLATION | 01-0.5"-CND1181-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1524 | PD-300A
01-VCND209 | INSTRUMENT ISOLATION | 01-0.5"-CND1181-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1525 | PD-300A
01-VCND210 | VENT VALVE | 01-0.75"-CND1243-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1526 | PD-054A
01-VCND211 | DRAIN VALVE | 01-0.75"-CND1927-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1527 | PD-300A
01-VCND212 | GLAND STEAM DSH SPRAY SUPPLY ISOLATION | 01-1"-CND1181-1EAA2A-1.0 "MIC | 1" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1528 | PD-300A
01-VCND213 | GLAND STEAM DSH SPRAY SUPPLY CHECK | 01-1"-CND1928-1EAA1A-1.0 "MIC | 1" | Check valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 790 | 310 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | PISTON CHECK; FLOW: 10 GPM (MIN), 50 GPM (MAX) | 1529 | PD-300A
01-VCND214 | LP DRAINS TANK SPRAY SUPPLY CV ISOLATION | 01-2.5"-CND1200-1EAA2A-1.0 "MOH | 2.5" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1530 | PD-305A
01-VCND215 | DRAIN VALVE | 01-0.75"-CND1288-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1531 | PD-305A
01-VCND221 | LP BYPASS SPRAY SUPPLY ISOLATION | 01-1.5"-CND1459-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1532 | PD-052A
01-VCND223 | CND TO CRH VENTILATOR SPRAY ISOLATION | 01-3"-CND1062-1EAA2A-1.0 "MIC | 3" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.2H | FLEXIBLE WEDGE | 1533 | PD-052A
01-VCND224 | HRH BYPASS SPRAY SUPPLY ISOLATION | 01-6"-CND1256-1EAA2A-1.0 "MIC | 6" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1534 | PD-052A
01-VCND225 | CND STRAINER ISOLATION | 01-8"-CND1256-1EAA2A-1.0 "MIC | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1535 | PD-052A
01-VCND226 | STRAINER DRAIN VALVE | 01-1.5"-CND1046-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1536 | PD-052A
01-VCND227 | CND STRAINER ISOLATION | 01-8"-CND1256-1EAA2A-1.0 "MIC | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1537 | PD-052A
01-VCND228 | CND STRAINER ISOLATION | 01-8"-CND1266-1EAA2A-1.0 "MIC | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1538 | PD-052A
01-VCND229 | STRAINER DRAIN VALVE | 01-1.5"-CND1048-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1539 | PD-052A
01-VCND230 | CND STRAINER ISOLATION | 01-8"-CND1266-1EAA2A-1.0 "MIC | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1540 | PD-052A
01-VCND231 | STRAINER VENT VALVE | 01-1.5"-CND1045-1EAA2A-1.0 "MIC | 1.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1541 | PD-052A
01-VCND232 | STRAINER VENT VALVE | 01-1.5"-CND1047-1EAA2A-1.0 "MIC | 1.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1542 | PD-052A
01-VCND233 | INSTRUMENT ISOLATION | 01-0.75"-CND1061-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1543 | PD-052A
01-VCND234 | INSTRUMENT ISOLATION | 01-0.75"-CND1061-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1544 | PD-052A
01-VCND235 | DEMIN FILL TO CND CHECK | 01-3"-CND1005-1ECA2A-1.0 "MOH | 3" | Check valve | CND | 1ECA2A | Water | CL600 | BE | BE | 790 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 100-250 GPM | 1545 | PD-052A
01-VCND236 | DEMIN FILL TO CND STOP CHECK | 01-3"-CND1005-1ECA2A-1.0 "MOH | 3" | Check Valve Locked Closed | CND | 1ECA2A | Water | CL600 | BE | BE | 790 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.01.1H | GLOBE STOP-CHECK; FLOW: 100-250 GPM | 1546 | PD-052A
01-VCND237 | DRAIN/HYDRO FILL VALVE | 01-0.75"-CND1005-1ECA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1ECA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-40S | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1547 | PD-052A
01-VCND238 | DEMIN FILL TO CND ISOLATION | 01-3"-CND1005-1ECA2A-1.0 "MOH | 3" | Globe valve | CND | 1ECA2A | Water | CL600 | BE | BE | 790 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.01.1H |  | 1548 | PD-052A
01-VCND239 | ECA COOLER PUMP DISCHARGE CHECK | 01-6"-CND1235-1EAA1A-1.0 "EOH | 6" | Check valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 100 GPM (MIN), 500 GPM (MAX) | 1549 | PD-054A
01-VCND240 | INSTRUMENT ISOLATION | 01-0.75"-CND1243-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1550 | PD-054A
01-VCND241 | ECA COOLER PUMP DISCHARGE CHECK | 01-6"-CND1259-1EAA1A-1.0 "EOH | 6" | Check valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 100 GPM (MIN), 500 GPM (MAX) | 1551 | PD-054A
01-VCND242 | ECA COOLING LOOP SUPPLY CHECK | 01-6"-CND1031-1EAA1A-1.0 "EOH | 6" | Check valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 100 GPM (MIN), 500 GPM (MAX) | 1552 | PD-054A
01-VCND243 | ECA COOLING LOOP MANUAL FLOW THROTTLING VALVE | 01-6"-CND1263-1EAA1A-1.0 "EOH | 6" | Globe valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H |  | 1553 | PD-054A
01-VCND244 | STEAM DRAINS PUMP SEAL WATER SUPPLY ISOLATION | 01-0.5"-CND1109-1BAA2A-1.0 "MOH | 0.5" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 1554 | PD-306A
01-VCND245 | STEAM DRAINS PUMP SEAL WATER SUPPLY THROTTLING VALVE | 01-0.5"-CND1109-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1555 | PD-306A
01-VCND247 | INSTRUMENT ISOLATION | 01-0.5"-CND1109-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1556 | PD-306A
01-VCND248 | STEAM DRAINS PUMP SEAL WATER SUPPLY CHECK | 01-0.5"-CND1109-1BAA2A-1.0 "MOH | 0.5" | Check valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | BALL CHECK; FLOW: 1-2 GPM | 1557 | PD-306A
01-VCND258 | VENT VALVE | 01-0.75"-CND1050-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1558 | PD-050A
01-VCND259 | DRAIN VALVE | 01-0.75"-CND1050-1BAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE, TO BE RATED FOR VACUUM SERVICE | 1559 | PD-050A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1560 | P&ID
01-VCND260 | DRAIN VALVE | 01-0.75"-CND1251-1EBB1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EBB1A | Water | CL800 | SWE | SWE | 790 | 380 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1561 | PD-034A
01-VCND261 | LP DRAINS TANK QUENCH TCV ISOLATION | 01-2.5"-CND1200-1EAA2A-1.0 "MOH | 2.5" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1562 | PD-305A
01-VCND262 | LP DRAINS TANK QUENCH TCV BYPASS VALVE | 01-2"-CND1201-1EAA2A-1.0 "MOH | 2" | Globe valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 1563 | PD-305A
01-VCND271 | STRAINER DRAIN | 01-0.5"-CND1002-1EAA2A-1.0 "MIC | 0.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 1564 | PD-052A
01-VCND272 | STEAM DRAINS PUMP SEAL WATER SUPPLY THROTTLING VALVE | 01-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1565 | PD-306A
01-VCND273 | VENT VALVE | 01-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1566 | PD-306A
01-VCND274 | INSTRUMENT ISOLATION | 01-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1567 | PD-306A
01-VCND275 | INSTRUMENT ISOLATION | 01-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1568 | PD-306A
01-VCND277 | STEAM DRAINS PUMP SEAL WATER SUPPLY CHECK | 01-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Check valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | BALL CHECK; FLOW: 1-2 GPM | 1569 | PD-306A
01-VCND278 | INSTRUMENT ISOLATION | 01-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1570 | PD-306A
01-VCND279 | STEAM DRAINS PUMP SEAL WATER SUPPLY THROTTLING VALVE | 01-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1571 | PD-306A
01-VCND280 | STEAM DRAINS PUMP SEAL WATER SUPPLY ISOLATION | 01-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 1572 | PD-306A
01-VCND301 | INSTRUMENT ISOLATION | 01-0.5"-CND1256-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1573 | PD-034A
01-VCND302 | INSTRUMENT ISOLATION | 01-0.5"-CND1014-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1574 | PD-034A
01-VCND307 | VENT VALVE | 01-0.75"-CND1258-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1575 | PD-034A
01-VCND308 | INSTRUMENT ISOLATION | 01-0.5"-CND1072-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1576 | PD-052A
01-VCND309 | LP ECONOMIZER BYPASS CV ISOLATION | 01-8"-CND1020-1EAA2A-1.0 "MOH | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1577 | PD-053A
01-VCND311 | ECA COOLER PUMP SUCTION ISOLATION | 01-6"-CND1031-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1578 | PD-054A
01-VCND312 | INSTRUMENT ISOLATION | 01-0.75"-CND1233-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1579 | PD-054A
01-VCND313 | ECA COOLER PUMP SUCTION ISOLATION | 01-6"-CND1233-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1580 | PD-054A
01-VCND314 | ECA COOLER PUMP DISCHARGE ISOLATION | 01-6"-CND1235-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1581 | PD-054A
01-VCND315 | INSTRUMENT ISOLATION | 01-0.75"-CND1235-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1582 | PD-054A
01-VCND320 | STRAINER VENT | 01-0.5"-CND1024-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1583 | PD-051A
01-VCND321 | INSTRUMENT ISOLATION | 01-0.5"-CND1152-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1584 | PD-052A
01-VCND322 | INSTRUMENT ISOLATION | 01-0.5"-CND1149-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1585 | PD-052A
01-VCND323 | CONDENSATE MIN RECIRC CV ISOLATION | 01-8"-CND1161-1EAA2A-1.0 "MOH | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1586 | PD-053A
01-VCND324 | ACC CURTAIN SPRAY CV ISOLATION | 01-4"-CND1038-1EAA2A-1.0 "MIC | 4" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1587 | PD-052A
01-VCND326 | ACC CURTAIN SPRAY CV ISOLATION | 01-4"-CND1038-1EAA2A-1.0 "MIC | 4" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1588 | PD-052A
01-VCND327 | ACC CURTAIN SPRAY CV BYPASS VALVE | 01-2"-CND1382-1EAA2A-1.0 "MIC | 2" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1589 | PD-052A
01-VCND328 | INSTRUMENT ISOLATION | 01-0.75"-CND1096-1DAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1DAA2A | Water | CL800 | SWE | SWE | 475 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1590 | PD-052A
01-VCND329 | CONDENSATE PUMP DISCHARGE ISOLATION | 01-10"-CND1017-1EAA2A-1.0 "MOH | 10" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1591 | PD-051A
01-VCND330 | STRAINER VENT VALVE | 01-0.5"-CND1023-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1592 | PD-051A
01-VCND333 | CND PUMP VENT VALVE | 01-1"-CND1022-1BAA2A-1.0 "MOH | 1" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1593 | PD-051A
01-VCND335 | INSTRUMENT ISOLATION | 01-0.75"-CND1259-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1594 | PD-054A
01-VCND337 | INSTRUMENT ISOLATION | 01-0.75"-CND1188-1DAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1DAA2A | Water | CL800 | SWE | SWE | 600 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1595 | PD-053A
01-VCND338 | INSTRUMENT ISOLATION | 01-0.75"-CND1188-1DAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1DAA2A | Water | CL800 | SWE | SWE | 600 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1596 | PD-053A
01-VCND339 | INSTRUMENT ISOLATION | 01-0.75"-CND1187-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1597 | PD-053A
01-VCND340 | ECA COOLER LOOP RETURN VALVE ISOLATION | 01-6"-CND1039-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1598 | PD-054A
01-VCND341 | DRAIN VALVE | 01-0.75"-CND1243-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1599 | PD-054A
01-VCND342 | INSTRUMENT ISOLATION | 01-0.75"-CND1259-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1600 | PD-054A
01-VCND343 | ECA COOLER LOOP RETURN VALVE ISOLATION | 01-6"-CND1039-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1601 | PD-054A
01-VCND344 | INSTRUMENT ISOLATION | 01-0.75"-CND1263-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1602 | PD-054A
01-VCND348 | DRAIN VALVE | 01-0.75"-CND1039-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1603 | PD-054A
01-VCND349 | DRAIN VALVE | 01-0.75"-CND1031-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1604 | PD-054A
01-VCND352 | ECA COOLER LOOP SUPPLY VALVE ISOLATION | 01-6"-CND1031-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1605 | PD-054A
01-VCND357 | INSTRUMENT ISOLATION | 01-0.75"-CND1031-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1606 | PD-054A
01-VCND359 | ECA COOLER PUMP DISCHARGE ISOLATION | 01-6"-CND1259-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1607 | PD-054A
01-VCND360 | STRAINER VENT VALVE | 01-0.5"-CND1054-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 1608 | PD-051A
01-VCND361 | STRAINER DRAIN VALVE | 01-2"-CND1016-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE, TO BE RATED FOR VACUUM SERVICE | 1609 | PD-051A
01-VCND362 | IRON FILTER DRAIN VALVE | 01-0.75"-CND1064-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1610 | PD-052A
01-VCND363 | DRAIN VALVE | 01-0.75"-CND1092-1EBB1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EBB1A | Water | CL800 | SWE | SWE | 790 | 380 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 1611 | PD-030A
01-VCND366 | HP DRAINS TANK QUENCH TCV BYPASS VALVE | 01-1.5"-CND1049-1EAA2A-1.0 "MOH | 1.5" | Globe valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 1612 | PD-304A
01-VCND367 | HP DRAINS TANK QUENCH TCV ISOLATION | 01-3"-CND1202-1EAA2A-1.0 "MOH | 3" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 1613 | PD-304A
01-VCND375 | INSTRUMENT ISOLATION | 01-0.75"-CND1187-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 1614 | PD-053A
01-VCND376 | VENT VALVE | 01-0.75"-CND1168-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1615 | PD-053A
01-VCND377 | DRAIN VALVE | 01-0.75"-CND1161-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0 | WEDGE GATE | 1616 | PD-053A
01-VCND378 | VENT VALVE | 01-0.75"-CND1033-1EBB1A-1.0 "MOH | 0.75" | Globe valve | CND | 1EBB1A | Water | CL1500 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1617 | PD-053A
01-VCND379 | VENT VALVE | 01-0.75"-CND1161-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 1618 | PD-053A
01-VCND380 | DRAIN VALVE | 01-0.75"-CND1258-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0 | WEDGE GATE | 1619 | PD-034A
01-VCND381 | VENT VALVE | 01-0.75"-CND1251-1EBB1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EBB1A | Water | CL1500 | SWE | SWE | 790 | 380 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 1620 | PD-034A
01-VCND400 | VENT VALVE | 01-1"-CND1055-1EAA2A-1.0 "MIC | 1" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1621 | PD-052A
01-VCND401 | VENT VALVE | 01-1"-CND1078-1EAA2A-1.0 "MIC | 1" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1622 | PD-052A
01-VCND402 | DRAIN VALVE | 01-1"-CND1081-1EAA2A-1.0 "MIC | 1" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H | WEDGE GATE | 1623 | PD-052A
01-VCND403 | DRAIN VALVE | 01-1"-CND1084-1EAA2A-1.0 "MIC | 1" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H | WEDGE GATE | 1624 | PD-052A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1625 | P&ID
01-VCND404 | VENT VALVE | 01-0.5"-CND1097-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 1626 | PD-053A
01-VCND405 | VENT VALVE | 01-0.75"-CND1096-1DAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1DAA2A | Water | CL800 | SWE | SWE | 475 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 1627 | PD-053A
01-VCND406 | STRAINER DRAIN VALVE | 01-0.75"-CND1181-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H | WEDGE GATE | 1628 | PD-300A
01-VCND407 | VENT VALVE | 01-0.75"-CND1263-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1629 | PD-054A
01-VCND408 | DRAIN VALVE | 01-0.75"-CND1263-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 1630 | PD-054A
01-VCND410 | VENT VALVE | 01-0.75"-CND1031-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1631 | PD-054A
01-VCND411 | VENT VALVE | 01-0.75"-CND1259-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 1632 | PD-054A
01-VCND420 | ECA COOLER PUMP DRAIN | 01-0.75"-CND1116-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL2500 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.03.3 |  | 1633 | PD-054A
01-VCND421 | ECA COOLER PUMP DRAIN | 01-0.75"-CND1114-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL2500 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.03.3 |  | 1634 | PD-054A
01-VCND576 | DRAIN VALVE | 01-0.75"-CND1892-1BAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 1635 | PD-053A
01-VCND577 | DRAIN VALVE | 01-0.75"-CND1890-1BAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 1636 | PD-053A
01-VCRH101 | CRH TO AXS BLOCK/CONTROL VALVE DRAIN VALVE | 01-0.75"-CRH1044-1EBB1A-2.5 "EIC | 0.75" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1637 | PD-030A
01-VCRH102 | PIT CONNECTION ROOT VALVE | 01-0.75"-CRH1101-1EBA1A-2.0 "EOH | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL1500 | SWE | SWE | 150 | 950 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1638 | PD-030A
01-VCRH103 | PIT CONNECTION BLOCK VALVE | 01-0.75"-CRH1101-1EBA1A-2.0 "EOH | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL1500 | SWE | SWE | 150 | 950 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1639 | PD-030A
01-VCRH104 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1049-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1640 | PD-030A
01-VCRH105 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1053-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1641 | PD-030A
01-VCRH106 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1052-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1642 | PD-030A
01-VCRH107 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1048-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1643 | PD-030A
01-VCRH108 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1046-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1644 | PD-030A
01-VCRH109 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1045-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1645 | PD-030A
01-VCRH110 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1047-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1646 | PD-030A
01-VCRH111 | DRIP LEG DRAIN | 01-2"-CRH1004-1EBA1A-2.0 "EOH | 2" | Ball valve | CRH | 1EBA1A | Steam | CL600 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 1647 | PD-031A
01-VCRH112 | DRIP LEG LS VENT/DRAIN VALVE | 01-1"-CRH1044-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1648 | PD-030A
01-VCRH115 | HYDRO/VENT CONNECTION VALVE | 01-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1649 | PD-031A
01-VCRH117 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1058-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1650 | PD-031A
01-VCRH120 | CRH TO AXS VENT VALVE | 01-0.75"-CRH1162-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1651 | PD-124A
01-VCRH121 | CRH TO AXS VENT VALVE | 01-0.75"-CRH1162-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1652 | PD-124A
01-VCRH122 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1057-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1653 | PD-031A
01-VCRH123 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1053-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1654 | PD-030A
01-VCRH124 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1057-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1655 | PD-031A
01-VCRH125 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1045-1EBB1A-2.5 "EIC | 0.75" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1656 | PD-030A
01-VCRH127 | DRIP LEG DRAIN | 01-2"-CRH1025-1EBB1A-3.5 "EIC | 2" | Ball valve | CRH | 1EBB1A | Steam | CL600 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 1657 | PD-030A
01-VCRH128 | PIT CONNECTION BLOCK VALVE | 01-0.75"-CRH1042-1EBB1A-2.5 "EIC | 0.75" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1658 | PD-030A
01-VCRH130 | DRIP LEG DRAIN | 01-2"-CRH1026-1EBA1A-2.0 "EOH | 2" | Ball valve | CRH | 1EBA1A | Steam | CL600 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 1659 | PD-030A
01-VCRH131 | VENTILATOR VALVE BLOCK VALVE | 01-10"-CRH1142-1EBB1A-4.5 "EIC | 10" | Gate valve | CRH | 1EBB1A | Steam | CL600 | BE | BE | 630 | 950 | S-60 | 4.5 " | No | 94.03.68.150.01.0H | PARALLEL SLIDE DISC, EXTERNAL BONNET DRAIN | 1660 | PD-030A
01-VCRH133 | DRIP LEG DRAIN VALVE | 01-2"-CRH1041-1EBB1A-3.5 "EIC | 2" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1661 | PD-030A
01-VCRH134 | DRIP LEG DRAIN VALVE | 01-2"-CRH1041-1EBB1A-3.5 "EIC | 2" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1662 | PD-030A
01-VCRH135 | DRIP LEG DRAIN VALVE | 01-2"-CRH1063-1EBA1A-2.0 "EOH | 2" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | - | 1663 | PD-030A
01-VCRH136 | DRIP LEG DRAIN VALVE | 01-2"-CRH1113-1EBA1A-2.0 "EOH | 2" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | - | 1664 | PD-031A
01-VCRH137 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1055-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1665 | PD-031A
01-VCRH138 | DRIP LEG DRAIN VALVE | 01-2"-CRH1063-1EBA1A-2.0 "EOH | 2" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | - | 1666 | PD-030A
01-VCRH139 | PTC CONNECTION | 01-0.75"-CRH1042-1EBB1A-3.5 "EIC | 0.75" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1667 | PD-030A
01-VCRH141 | PIT CONNECTION BLOCK VALVE | 01-0.75"-CRH1101-1EBA1A-2.0 "EOH | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL1500 | SWE | SWE | 150 | 950 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1668 | PD-030A
01-VCRH142 | PIT CONNECTION BLOCK VALVE | 01-0.75"-CRH1101-1EBA1A-2.0 "EOH | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL1500 | SWE | SWE | 150 | 950 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1669 | PD-030A
01-VCRH143 | PIT CONNECTION BLOCK VALVE | 01-0.75"-CRH1042-1EBB1A-2.5 "EIC | 0.75" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1670 | PD-030A
01-VCRH144 | PIT CONNECTION BLOCK VALVE | 01-0.75"-CRH1042-1EBB1A-3.5 "EIC | 0.75" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1671 | PD-030A
01-VCRH146 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1056-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1672 | PD-031A
01-VCRH147 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1056-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1673 | PD-031A
01-VCRH148 | PT CONNECTION ROOT VALVE | 01-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1674 | PD-031A
01-VCRH150 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1045-1EBB1A-2.5 "EIC | 0.75" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1675 | PD-030A
01-VCRH151 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1044-1EBB1A-2.5 "EIC | 0.75" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1676 | PD-030A
01-VCRH154 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1052-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1677 | PD-030A
01-VCRH155 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1049-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1678 | PD-030A
01-VCRH156 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1048-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1679 | PD-030A
01-VCRH157 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1053-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1680 | PD-030A
01-VCRH158 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1048-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1681 | PD-030A
01-VCRH159 | HYDRO/VENT CONNECTION VALVE | 01-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1682 | PD-031A
01-VCRH160 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1048-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1683 | PD-030A
01-VCRH161 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1053-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1684 | PD-030A
01-VCRH162 | CRH TO AXS VENT VALVE | 01-0.75"-CRH1162-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1685 | PD-124A
01-VCRH165 | HYDRO/VENT CONNECTION VALVE | 01-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1686 | PD-031A
01-VCRH166 | FIT/FE ROOT VALVE | 01-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1687 | PD-031A
01-VCRH169 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1055-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1688 | PD-031A
01-VCRH170 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1058-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H |  | 1689 | PD-031A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1690 | P&ID
01-VCRH171 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1056-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1691 | PD-031A
01-VCRH172 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1057-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1692 | PD-031A
01-VCRH173 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1056-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1693 | PD-031A
01-VCRH174 | DRIP LEG LS VENT/DRAIN VALVE | 01-0.75"-CRH1057-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 1694 | PD-031A
01-VCRH175 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1046-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1695 | PD-030A
01-VCRH176 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1047-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1696 | PD-030A
01-VCRH177 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1045-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1697 | PD-030A
01-VCRH178 | DRIP LEG LS ROOT VALVE | 01-1"-CRH1044-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 1698 | PD-030A
01-VCRH180 | CRH TO AXS ISOLATION | 01-3"-CRH1193-1EBA1A-2.5 "EOC | 3" | Gate valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 2.5 " | No | 94.03.68.150.01.1H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 1699 | PD-124A
01-VCRH181 | CRH TO AXS ISOLATION | 01-4"-CRH1162-1EBA1A-2.5 "EOC | 4" | Gate valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 2.5 " | No | 94.03.68.150.01.1H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 1700 | PD-124A
01-VCRH182 | CRH TO AXS VENT VALVE | 01-0.75"-CRH1162-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1701 | PD-124A
01-VCRH183 | CRH TO AXS ISOLATION | 01-4"-CRH1193-1EBA1A-2.5 "EOC | 4" | Gate valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 2.5 " | No | 94.03.68.150.01.1H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 1702 | PD-124A
01-VCRH184 | CRH TO AXS ISOLATION | 01-6"-CRH1162-1EBA1A-3.0 "EOC | 6" | Gate valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 3.0 " | No | 94.03.68.150.01.1H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 1703 | PD-124A
01-VCRH185 | DRIP LEG DRAIN | 01-2"-CRH1113-1EBA1A-2.0 "EOH | 2" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | - | 1704 | PD-031A
01-VCRH186 | HYDRO/VENT CONNECTION VALVE | 01-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1705 | PD-031A
01-VCTP100 | UNIT 1 WATER WASH TANK INLET ISOLATION | 01-10"-CTP0101-1ADA2U | 10" | Gate valve | CTP | 1ADA2U | Water | CL150 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 |  | 1706 | PD-332
01-VCTP101 | UNIT 1 ECA COOLER DRAIN VALVE (B) ISOLATION | 01-1"-CTP1041-1DAA1A-1.5 "EOI | 1" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 662 | S-80 | 1.5 " | No | 94.03.68.150.06.2H |  | 1707 | PD-335A
01-VCTP102 | DRAIN ISOLATION | 01-0.75"-CTP1083-1DBA1A-2.5 "EOH | 0.75" | Globe valve | CTP | 1DBA1A | Air/Water | CL800 | SWE | SWE | 74 | 1040 | S-80 | 2.5 " | Yes | 94.03.68.150.06.3H |  | 1708 | PD-336A
01-VCTP103 | UNIT 1 BLADE RING DRAIN ISOLATION | 01-2"-CTP1003-1EAA1A-1.0 "EOI | 2" | Gate valve | CTP | 1EAA1A | Air/Water | CL800 | SWE | SWE | 682 | 482 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1709 | PD-335A
01-VCTP104 | UNIT 1 ECA DRAIN MIST DEPARATOR DRAIN VALVE (B) ISOLATION | 01-1"-CTP1042-1DAA1A-1.0 "EOI | 1" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 1710 | PD-335A
01-VCTP105 | UNIT 1 BLADE COMBUSTOR ISOLATION | 01-1"-CTP1005-1EAA1A-1.0 "EOI | 1" | Gate valve | CTP | 1EAA1A | Air/Water | CL800 | SWE | SWE | 682 | 482 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 1711 | PD-335A
01-VCTP106 | UNIT 1 ECA DRAIN MIST DEPARATOR DRAIN VALVE (A) ISOLATION | 01-2"-CTP1050-1DAA1A-1.0 "EOI | 2" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 1712 | PD-335A
01-VCTP107 | UNIT 1 ECA COOLER DRAIN VALVE (A) ISOLATION | 01-2"-CTP1077-1DAA1A-1.5 "EOI | 2" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 662 | S-80 | 1.5 " | No | 94.03.68.150.06.2H |  | 1713 | PD-335A
01-VCTP108 | UNIT 1 COOLING AIR COOLER (HIGH TEMP) DRAIN VALVE (B) ISOLATION | 01-1"-CTP1057-1DAA1A-1.5 "EOI | 1" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 752 | S-80 | 1.5 " | No | 94.03.68.150.06.2H |  | 1714 | PD-335A
01-VCTP109 | UNIT 1 COOLING AIR COOLER (HIGH TEMP) DRAIN VALVE (A) ISOLATION | 01-2"-CTP1073-1DAA1A-1.0 "EOI | 2" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 509 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 1715 | PD-335A
01-VCTP110 | UNIT 1 COOLING AIR COOLER (LOW TEMP) DRAIN VALVE (A) ISOLATION | 01-2"-CTP1046-1DAA1A-2.0 "EOI | 2" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 752 | S-80 | 2.0 " | No | 94.03.68.150.06.2H |  | 1716 | PD-335A
01-VCTP111 | UNIT 1 COOLING AIR COOLER (LOW TEMP) DRAIN VALVE (B) ISOLATION | 01-1"-CTP1071-1DAA1A-1.0 "EOI | 1" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 509 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 1717 | PD-335A
01-VCTP113 | UNIT 1 2C COOLER DRAIN VALVE ISOLATION | 01-4"-CTP1091-1DBB1A-4.0 "EII | 4" | Gate valve | CTP | 1DBB1A | Air/Water | CL300 | BE | BE | 283 | 968 | S-40 | 4.0 " | No | 94.03.68.150.03.2H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 1718 | PD-336A
01-VCTP114 | DRAIN ISOLATION | 01-0.75"-CTP1068-1BAA1A-1.0 "MII | 0.75" | Ball valve | CTP | 1BAA1A | AIR/OIL | CL600 | SWE | SWE | 15 | 194 | S-80 | 1.0 " | No | 94.03.68.150.06.1 |  | 1719 | PD-334A
01-VCTP115 | DRAIN ISOLATION | 01-0.75"-CTP1092-1BCA2A | 0.75" | Ball valve | CTP | 1BCA2A | AIR | CL600 | SWE | SWE | 145 | 212 | S-40S |  | No | 94.03.68.150.06.1 |  | 1720 | PD-336A
01-VCTP116 | DRAIN ISOLATION | 01-0.75"-CTP1066-1BCA2A | 0.75" | Ball valve | CTP | 1BCA2A | AIR | CL600 | SWE | SWE | 145 | 212 | S-40S |  | No | 94.03.68.150.06.1 |  | 1721 | PD-336A
01-VCTP117 | COOLING AIR TO FUEL GAS NOZZLE ISOLATION | 01-6"-CTP1066-1BCA2A | 6" | Butterfly valve | CTP | 1BCA2A | AIR | CL150 | LUGGED | LUGGED | 145 | 212 | S-10S |  | No | 94.03.68.150.04.1 | INDOOR INSTALLATION PER PIPE ROUTING, PROVIDE 20 FT CHAIN WHEEL OPERATOR | 1722 | PD-336A
01-VCTP119 | INSTRUMENT ISOLATION | 01-0.75"-CTP1023-1BCA2A | 0.75" | Globe valve | CTP | 1BCA2A | Water | CL800 | SWE | SWE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.2H |  | 1723 | PD-332
01-VCTP120 | DRAIN ISOLATION | 01-0.75"-CTP1004-1BAA1A-1.0 "MII | 0.75" | Ball valve | CTP | 1BAA1A | AIR/OIL | CL600 | SWE | SWE | 15 | 194 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 1724 | PD-334A
01-VCTP121 | UNIT 1 ON LINE WASH SUPPLY ISOLATION AT CT PACKAGE | 01-3"-CTP1023-1BCA2A | 3" | Ball valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 195 | 140 | S-10S |  | No | 94.03.68.150.03.1 |  | 1725 | PD-332
01-VCTP123 | UNIT 1 ON LINE WASH CLEANING 3 WAY VALVE | 01-3"-CTP1023-1BCA2A | 3" | 3-way valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 195 | 140 | S-10S |  | No | 94.03.68.150.03.1 | T-Port Ball Valve | 1726 | PD-332
01-VCTP125 | UNIT 1 ON LINE WASH SUPPLY ISOLATION AT WW SKID | 01-3"-CTP1035-1BCA2A | 3" | Ball valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 195 | 140 | S-10S |  | No | 94.03.68.150.03.1 |  | 1727 | PD-332
01-VCTP129 | INSTRUMENT ISOLATION | 01-0.75"-CTP1033-1BCA2A | 0.75" | Globe valve | CTP | 1BCA2A | Water | CL800 | SWE | SWE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.2H |  | 1728 | PD-332
01-VCTP131 | UNIT 1 OFF LINE WASH SUPPLY ISOLATION AT CT PACKAGE | 01-3"-CTP1033-1BCA2A | 3" | Ball valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 195 | 140 | S-10S |  | No | 94.03.68.150.03.1 |  | 1729 | PD-332
01-VCTP133 | UNIT 1 OFF LINE WASH CLEANING 3 WAY VALVE | 01-3"-CTP1033-1BCA2A | 3" | 3-way valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 195 | 140 | S-10S |  | No | 94.03.68.150.03.1 | T-Port Ball Valve | 1730 | PD-332
01-VCTP135 | UNIT 1 OFF LINE WASH SUPPLY ISOLATION AT WW SKID | 01-3"-CTP1025-1BCA2A | 3" | Ball valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 195 | 140 | S-10S |  | No | 94.03.68.150.03.1 |  | 1731 | PD-332
01-VCTP146 | DRAIN ISOLATION | 01-0.75"-CTP1081-1DBA1A-2.5 "EOH | 0.75" | Globe valve | CTP | 1DBA1A | Air/Water | CL800 | SWE | SWE | 74 | 1040 | S-80 | 2.5 " | Yes | 94.03.68.150.06.3H |  | 1732 | PD-336A
01-VCTP179 | DRAIN ISOLATION | 01-0.75"-CTP1070-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 1733 | PD-333A
01-VCTP180 | DRAIN ISOLATION | 01-0.75"-CTP1049-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 1734 | PD-333A
01-VCTP181 | DRAIN ISOLATION | 01-0.75"-CTP1019-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 1735 | PD-333A
01-VCTP182 | DRAIN ISOLATION | 01-0.75"-CTP1029-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 1736 | PD-333A
01-VCTP183 | DRAIN ISOLATION | 01-0.75"-CTP1039-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 1737 | PD-333A
01-VCTP185 | INSTRUMENT ISOLATION | 01-0.75"-CTP1060-1BCA2A-1.0 "MOH | 0.75" | Globe valve | CTP | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.2H |  | 1738 | PD-333A
01-VDWS100 | CALCITE FILTER SUPPLY CHECK | 01-3"-DWS1005-1BCA2A | 3" | Check valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S |  | No | 94.03.68.150.03.0 | SWING; MAX FLOW 850 GPM; MIN FLOW 50 GPM | 1739 | PD-333A
01-VDWS101 | INSTRUMENT | 01-0.75"-DWS1001-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 |  | 1740 | PD-333A
01-VDWS102 | UNIT 1 PHOSPHATE SILUTION SUPPLY ISOLATION | 01-1"-DWS1002-1BCA2A-1.0 "MOH | 1" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1741 | PD-411
01-VDWS103 | UNIT 1 SAMPLE PANEL SUPPLY | 01-1"-DWS1004-1BCA2A-1.0 "MOH | 1" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1742 | PD-411
01-VDWS104 | UNIT 1 EVAP COOLER SUPPLY ISOLATION | 01-3"-DWS1001-1BCA2A | 3" | Gate valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S |  | No | 94.03.68.150.03.2H |  | 1743 | PD-333A
01-VDWS105 | VENT | 01-0.75"-DWS1015-1BCA2A-1.0 "MOH | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.3H |  | 1744 | PD-050A
01-VDWS106 | CALCITE FILTER ISOLATION | 01-1"-DWS1011-1BCA2A | 1" | Gate valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 | FLEXIBLE WEDGE | 1745 | PD-333A
01-VDWS107 | CALCITE FILTER CO2 INJECTION MODULE ISOLATION | 01-1"-DWS1010-1BCA2A | 1" | Gate valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 | FLEXIBLE WEDGE | 1746 | PD-333A
01-VDWS108 | DRAIN | 01-0.75"-DWS1012-1BCA2A | 0.75" | Gate valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.2H |  | 1747 | PD-333A
01-VDWS109 | INSTRUMENT | 01-0.75"-DWS1013-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.2H |  | 1748 | PD-333A
01-VDWS110 | INSTRUMENT | 01-0.75"-DWS1013-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.2H |  | 1749 | PD-333A
01-VDWS614 | INSTRUMENT | 01-0.5"-DWS1007-1BCA2A-1.0 "MOH | 0.5" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.2H |  | 1750 | PD-270A
01-VDWS615 | INSTRUMENT | 01-0.5"-DWS1008-1BCA2A-1.0 "MOH | 0.5" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.2H |  | 1751 | PD-270A
01-VDWS616 | CCW HEAD TANK SUPPLY CHECK | 01-2"-DWS1003-1BCA2A-1.0 "MOH | 2" | Check valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1752 | PD-270A
01-VDWS617 | CCW HEAD TANK ISOLATION | 01-2"-DWS1003-1BCA2A-1.0 "MOH | 2" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1753 | PD-270A
01-VDWS620 | VENT | 01-0.75"-DWS1003-1BCA2A-1.0 "MOH | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1754 | PD-270A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1755 | P&ID
01-VDWS636 | CONTROL VALVE ISOLATION | 01-0.75"-DWS1014-1BCA2A-1.0 "MOH | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.3H |  | 1756 | PD-050A
01-VDWS638 | CONTROL VALVE ISOLATION | 01-4"-DWS1017-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 1757 | PD-050A
01-VDWS639 | CONTROL VALVE ISOLATION | 01-4"-DWS1017-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 1758 | PD-050A
01-VDWS641 | CONTROL VALVE ISOLATION | 01-6"-DWS1006-1BCA2A-1.0 "MOH | 6" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 1759 | PD-050A
01-VDWS642 | CONTROL VALVE ISOLATION | 01-6"-DWS1006-1BCA2A-1.0 "MOH | 6" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 1760 | PD-050A
01-VDWS643 | DRAIN | 01-0.75"-DWS1006-1BCA2A-1.0 "MOH | 0.75" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1761 | PD-050A
01-VDWS648 | DRAIN | 01-0.75"-DWS1017-1BCA2A-1.0 "MOH | 0.75" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 1762 | PD-050A
01-VFGS113 | FLOW METER INLET | 01-10"-FGS1125-1EAL1A-1.0 "MOC | 10" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 302 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 1763 | PD-655A
01-VFGS115 | N2 PURGE ISOLATION | 01-0.75"-FGS1030-1EAL1A-1.0 "EOC | 0.75" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1764 | PD-656A
01-VFGS116 | VENT/DRAIN | 01-0.75"-FGS1125-1EAL1A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 302 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1765 | PD-655A
01-VFGS120 | N2 PURGE ISOLATION | 01-0.75"-FGS1077-1BAA2A-1.0 "AS | 0.75" | Ball valve | FGS | 1BAA2A | Natural Gas | CL600 | SWE | SWE | 75 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1766 | PD-658A
01-VFGS122 | FLOW METER BYPASS | 01-10"-FGS1018-1EAL1A-1.0 "MOC | 10" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 302 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 1767 | PD-655A
01-VFGS123 | EMERGENCY VENT VALVE BYPASS | 01-3"-FGS1035-1EAL1A-1.0 "EOC | 3" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 1768 | PD-656A
01-VFGS124 | TO GT EMERGENCY SHUT OFF VALVE | 01-10"-FGS1125-1EAL1A-1.0 "MOC | 10" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 302 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 1769 | PD-655A
01-VFGS128 | DRAIN | 01-1"-FGS1027-1EAL1A-1.0 "EOC | 1" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1770 | PD-656A
01-VFGS130 | PERFORMANCE HEATER TO EMERGENCY VENT VALVE | 01-3"-FGS1030-1EAL1A-1.0 "EOC | 3" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 1771 | PD-656A
01-VFGS134 | DRAIN | 01-1"-FGS1025-1EAL1A-1.0 "EOC | 1" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1772 | PD-656A
01-VFGS140 | INSTRUMENTATION ROOT VALVE | 01-0.75"-FGS1040-1EAL1A-1.0 "EOC | 0.75" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1773 | PD-656A
01-VFGS141 | INSTRUMENTATION ROOT VALVE | 01-0.75"-FGS1040-1EAL1A-1.0 "EOC | 0.75" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1774 | PD-656A
01-VFGS143 | N2 PURGE ISOLATION | 01-1"-FGS1074-1EAL1A-1.0 "EOC | 1" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1775 | PD-657A
01-VFGS147 | INSTRUMENT | 01-1"-FGS1092-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 1776 | PD-657A
01-VFGS148 | INSTRUMENTATION ROOT VALVE | 01-1"-FGS1092-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 1777 | PD-657A
01-VFGS157 | INSTRUMENTATION ROOT VALVE | 01-1"-FGS1092-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 1778 | PD-657A
01-VFGS158 | INSTRUMENTATION ROOT VALVE | 01-1"-FGS1092-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 1779 | PD-657A
01-VFGS174 | GAS TURBINE FUEL GAS CARTRIDGE FILTER INLET | 01-12"-FGS1074-1EAL1A-1.5 "EOC | 12" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-XS | 1.5 " | No | 94.03.68.150.07.0 |  | 1780 | PD-657A
01-VFGS176 | EQUIPMENT ISOLATION | 01-6"-FGS1076-1EAL2A-1.0 "MOC | 6" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1781 | PD-658A
01-VFGS177 | VENT | 01-2"-FGS1078-1ECD1A-1.0 "EOC | 2" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 698 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 1782 | PD-657A
01-VFGS178 | VENT | 01-2"-FGS1078-1ECD1A-1.0 "EOC | 2" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 698 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 1783 | PD-657A
01-VFGS179 | EQUIPMENT ISOLATION | 01-12"-FGS1077-1BAA2A-2.0 "AS | 12" | Ball valve | FGS | 1BAA2A | Natural Gas | CL150 | RFFE | RFFE | 75 | 130 | S-STD | 2.0 " | No | 94.03.68.150.07.0 |  | 1784 | PD-658A
01-VFGS184 | VENT | 01-2"-FGS1080-1ECD1A-1.0 "EOC | 2" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 698 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 1785 | PD-657A
01-VFGS192 | FUEL GAS PURGE CREDIT SHUT OFF VALVE A | 01-12"-FGS1092-1ECD1A-1.5 "EOC | 12" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-80S | 1.5 " | No | 94.03.68.150.07.0 |  | 1786 | PD-657A
01-VFGS193 | VENT | 01-1"-FGS1094-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 1787 | PD-657A
01-VFGS217 | N2 PURGE ISOLATION | 01-0.75"-FGS1076-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 1788 | PD-658A
01-VHPS100 | PIT ROOT VALVE | 01-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 1789 | PD-021A
01-VHPS101 | PIT ROOT VALVE | 01-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 1790 | PD-021A
01-VHPS102 | PIT ROOT VALVE | 01-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 1791 | PD-021A
01-VHPS103 | PIT ROOT VALVE | 01-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 1792 | PD-021A
01-VHPS106 | PTC ROOT VALVE | 01-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 1793 | PD-021A
01-VHPS107 | PTC ROOT VALVE | 01-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 1794 | PD-021A
01-VHPS108 | DRIP LEG DRAIN | 01-2"-HPS1015-1HBD2A-4.0 "EIC | 2" | Ball valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 4.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 1795 | PD-021A
01-VHPS109 | DRIP LEG DRAIN VALVE | 01-2"-HPS1003-1HBD2A-4.0 "EIC | 2" | Gate valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 4.0 " | No | 94.03.68.150.02.0H | FULL BORE | 1796 | PD-021A
01-VHPS110 | DRIP LEG DRAIN VALVE | 01-2"-HPS1003-1HBD2A-4.0 "EIC | 2" | Gate valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 4.0 " | No | 94.03.68.150.02.0H | FULL BORE | 1797 | PD-021A
01-VHPS111 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1798 | PD-020A
01-VHPS112 | PTC ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1799 | PD-020A
01-VHPS113 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1800 | PD-020A
01-VHPS114 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1801 | PD-020A
01-VHPS115 | PTC ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1802 | PD-020A
01-VHPS116 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1803 | PD-020A
01-VHPS119 | PIT ROOT VALVE | 01-0.75"-HPS1151-1EBA1A-1.5 "EOC | 0.75" | Globe valve | HPS | 1EBA1A | Steam | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1804 | PD-020A
01-VHPS120 | PIT ROOT VALVE | 01-0.75"-HPS1151-1EBA1A-1.5 "EOC | 0.75" | Globe valve | HPS | 1EBA1A | Steam | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1805 | PD-020A
01-VHPS121 | PIT ROOT VALVE | 01-0.75"-HPS1151-1EBA1A-1.5 "EOC | 0.75" | Globe valve | HPS | 1EBA1A | Steam | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1806 | PD-020A
01-VHPS122 | PIT ROOT VALVE | 01-0.75"-HPS1151-1EBA1A-1.5 "EOC | 0.75" | Globe valve | HPS | 1EBA1A | Steam | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 1807 | PD-020A
01-VHPS123 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1808 | PD-020A
01-VHPS124 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1809 | PD-020A
01-VHPS125 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H |  | 1810 | PD-020A
01-VHPS126 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1811 | PD-020A
01-VHPS127 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1812 | PD-020A
01-VHPS128 | PIT ROOT VALVE | 01-0.75"-HPS1163-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HPS | 1FBD1A | Steam | CL1500 | SWE | SWE | 630 | 1097 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 1813 | PD-020A
01-VHPS129 | PIT ROOT VALVE | 01-0.75"-HPS1163-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HPS | 1FBD1A | Steam | CL1500 | SWE | SWE | 630 | 1097 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 1814 | PD-020A
01-VHPS130 | PIT ROOT VALVE | 01-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1815 | PD-020A
01-VHPS137 | VENT VALVE | 01-0.75"-HPS1174-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1816 | PD-020A
01-VHPS138 | VENT VALVE | 01-0.75"-HPS1174-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 1817 | PD-020A
01-VHRH100 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1818 | PD-034A
01-VHRH101 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 1819 | PD-034A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1820 | P&ID
01-VHRH102 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1821 | PD-034A
01-VHRH103 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1822 | PD-034A
01-VHRH104 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1823 | PD-034A
01-VHRH105 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1114-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.3H |  | 1824 | PD-034A
01-VHRH106 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1825 | PD-034A
01-VHRH107 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 1826 | PD-034A
01-VHRH108 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1827 | PD-035A
01-VHRH109 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1828 | PD-035A
01-VHRH110 | DRIP LEG DRAIN | 01-2"-HRH1112-1FBD1A-4.0 "EIC | 2" | Ball valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 1829 | PD-034A
01-VHRH111 | 01-IKS-HRH100F ISOLATION VALVE | 01-0.75"-HRH1114-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.3H |  | 1830 | PD-034A
01-VHRH113 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1114-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1831 | PD-034A
01-VHRH114 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1114-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1832 | PD-034A
01-VHRH115 | WARMING LINE ISOLATION | 01-2"-HRH1114-1FBD1A-4.0 "EIC | 2" | Gate valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.02.0H | - | 1833 | PD-034A
01-VHRH116 | WARMING LINE ISOLATION | 01-2"-HRH1114-1FBD1A-4.0 "EIC | 2" | Gate valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.02.0H | - | 1834 | PD-034A
01-VHRH120 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-2"-HRH1111-1FBD1A-4.0 "EIC | 2" | Gate valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.02.0H | VALVE TO BE FULL PORT (I.E. 100% BORE AREA) | 1835 | PD-034A
01-VHRH121 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 1836 | PD-034A
01-VHRH125 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1121-1EBD1A-2.5 "EOH | 0.75" | Globe valve | HRH | 1EBD1A | Steam | CL800 | SWE | SWE | 150 | 1096 | S-80 | 2.5 " | Yes | 94.03.68.150.02.0H | - | 1837 | PD-034A
01-VHRH126 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1121-1EBD1A-2.5 "EOH | 0.75" | Globe valve | HRH | 1EBD1A | Steam | CL800 | SWE | SWE | 150 | 1096 | S-80 | 2.5 " | Yes | 94.03.68.150.02.0H | - | 1838 | PD-034A
01-VHRH135 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 1839 | PD-034A
01-VHRH136 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 1840 | PD-034A
01-VHRH137 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-2"-HRH1111-1FBD1A-4.0 "EIC | 2" | Gate valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.02.0H | VALVE TO BE FULL PORT (I.E. 100% BORE AREA) | 1841 | PD-034A
01-VHRH187 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 1842 | PD-034A
01-VHRH188 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 1843 | PD-034A
01-VINA100 | END USER ISOLATION | 01-1"-INA1101-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1844 | PD-552
01-VINA101 | STUB-UP ISOLATION | 01-1"-INA1029-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1845 | PD-557
01-VINA102 | END USER ISOLATION | 01-0.75"-INA1090-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1846 | PD-552
01-VINA103 | STUB-UP ISOLATION | 01-1"-INA1025-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1847 | PD-557
01-VINA104 | STUB-UP ISOLATION | 01-1"-INA1015-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1848 | PD-553
01-VINA105 | DRAIN | 01-0.75"-INA1039-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1849 | PD-558
01-VINA106 | DRAIN | 01-0.75"-INA1501-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1850 | PD-552
01-VINA107 | DRAIN | 01-0.75"-INA1096-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1851 | PD-557
01-VINA108 | END USER ISOLATION | 01-0.75"-INA1329-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1852 | PD-559
01-VINA109 | END USER ISOLATION | 01-0.75"-INA1327-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1853 | PD-559
01-VINA110 | END USER ISOLATION | 01-0.75"-INA1062-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1854 | PD-552
01-VINA111 | END USER ISOLATION | 01-0.75"-INA1330-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1855 | PD-559
01-VINA112 | END USER ISOLATION | 01-0.75"-INA1054-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1856 | PD-552
01-VINA113 | END USER ISOLATION | 01-0.75"-INA1313-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1857 | PD-559
01-VINA114 | END USER ISOLATION | 01-0.75"-INA1038-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1858 | PD-552
01-VINA115 | STUB-UP ISOLATION | 01-1.5"-INA1031-1KFD1A | 1.5" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1859 | PD-557
01-VINA116 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1055-1DCD1A-1.0 "EOI | 0.75" | Globe valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 1860 | PD-552
01-VINA117 | END USER ISOLATION | 01-0.75"-INA1328-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1861 | PD-559
01-VINA118 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1055-1DCD1A-1.0 "EOI | 0.75" | Y stop check valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 1862 | PD-552
01-VINA119 | END USER ISOLATION | 01-0.75"-INA1127-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1863 | PD-552
01-VINA120 | END USER ISOLATION | 01-0.75"-INA1334-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1864 | PD-559
01-VINA121 | END USER ISOLATION | 01-0.75"-INA1333-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1865 | PD-559
01-VINA122 | END USER ISOLATION | 01-0.75"-INA1006-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1866 | PD-552
01-VINA123 | END USER ISOLATION | 01-1"-INA1575-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1867 | PD-553
01-VINA124 | STUB-UP ISOLATION | 01-1"-INA1042-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1868 | PD-552
01-VINA125 | END USER ISOLATION | 01-0.75"-INA1325-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1869 | PD-559
01-VINA126 | STUB-UP ISOLATION | 01-1"-INA1101-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1870 | PD-552
01-VINA127 | END USER ISOLATION | 01-0.75"-INA1314-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1871 | PD-560
01-VINA128 | STUB-UP ISOLATION | 01-1"-INA1092-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1872 | PD-552
01-VINA129 | END USER ISOLATION | 01-0.75"-INA1250-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1873 | PD-559
01-VINA130 | STUB-UP ISOLATION | 01-1"-INA1033-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1874 | PD-552
01-VINA131 | END USER ISOLATION | 01-0.75"-INA1691-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1875 | PD-557
01-VINA132 | END USER ISOLATION | 01-0.75"-INA1072-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1876 | PD-557
01-VINA133 | END USER ISOLATION | 01-0.75"-INA1335-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1877 | PD-559
01-VINA134 | END USER ISOLATION | 01-0.75"-INA1679-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1878 | PD-557
01-VINA135 | END USER ISOLATION | 01-1"-INA1474-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1879 | PD-559
01-VINA136 | END USER ISOLATION | 01-0.75"-INA1379-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1880 | PD-559
01-VINA137 | END USER ISOLATION | 01-0.75"-INA1075-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1881 | PD-557
01-VINA138 | END USER ISOLATION | 01-0.75"-INA1076-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1882 | PD-557
01-VINA139 | END USER ISOLATION | 01-2"-INA1019-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1883 | PD-559
01-VINA140 | END USER ISOLATION | 01-0.75"-INA1052-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1884 | PD-552
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1885 | P&ID
01-VINA141 | STUB-UP ISOLATION | 01-1"-INA1116-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1886 | PD-552
01-VINA142 | END USER ISOLATION | 01-1"-INA1501-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1887 | PD-552
01-VINA143 | END USER ISOLATION | 01-0.75"-INA1383-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1888 | PD-559
01-VINA144 | STUB-UP ISOLATION | 01-1"-INA1686-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1889 | PD-557
01-VINA145 | END USER ISOLATION | 01-0.75"-INA1385-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1890 | PD-559
01-VINA146 | END USER ISOLATION | 01-0.75"-INA1039-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1891 | PD-558
01-VINA147 | END USER ISOLATION | 01-0.75"-INA1386-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1892 | PD-559
01-VINA148 | END USER ISOLATION | 01-0.75"-INA1387-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1893 | PD-559
01-VINA149 | END USER ISOLATION | 01-0.75"-INA1249-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1894 | PD-552
01-VINA150 | STUB-UP ISOLATION | 01-1"-INA1121-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1895 | PD-552
01-VINA151 | DRAIN | 01-0.75"-INA1399-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1896 | PD-559
01-VINA152 | END USER ISOLATION | 01-0.75"-INA1689-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1897 | PD-559
01-VINA153 | END USER ISOLATION | 01-0.75"-INA1460-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1898 | PD-557
01-VINA154 | STUB-UP ISOLATION | 01-2"-INA1082-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1899 | PD-552
01-VINA155 | DRAIN | 01-0.75"-INA1018-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1900 | PD-559
01-VINA156 | STUB-UP ISOLATION | 01-2"-INA1086-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1901 | PD-552
01-VINA157 | END USER ISOLATION | 01-0.75"-INA1456-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1902 | PD-559
01-VINA158 | STUB-UP ISOLATION | 01-2"-INA1091-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1903 | PD-552
01-VINA159 | END USER ISOLATION | 01-0.75"-INA1454-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1904 | PD-558
01-VINA160 | END USER ISOLATION | 01-0.75"-INA1469-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1905 | PD-558
01-VINA161 | END USER ISOLATION | 01-0.75"-INA1470-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1906 | PD-558
01-VINA162 | END USER ISOLATION | 01-0.75"-INA1471-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1907 | PD-558
01-VINA163 | END USER ISOLATION | 01-0.75"-INA1472-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1908 | PD-558
01-VINA164 | END USER ISOLATION | 01-0.75"-INA1473-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1909 | PD-559
01-VINA165 | END USER ISOLATION | 01-0.75"-INA1040-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1910 | PD-558
01-VINA166 | END USER ISOLATION | 01-0.75"-INA1248-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1911 | PD-552
01-VINA167 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1055-1DCD1A-1.0 "EOI | 0.75" | Check valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 1912 | PD-552
01-VINA168 | END USER ISOLATION | 01-0.75"-INA1477-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1913 | PD-559
01-VINA169 | END USER ISOLATION | 01-0.75"-INA1041-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1914 | PD-552
01-VINA170 | END USER ISOLATION | 01-0.75"-INA1479-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1915 | PD-559
01-VINA171 | END USER ISOLATION | 01-0.75"-INA1046-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1916 | PD-552
01-VINA172 | END USER ISOLATION | 01-0.75"-INA1481-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1917 | PD-558
01-VINA173 | DRAIN | 01-0.75"-INA1398-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1918 | PD-558
01-VINA174 | END USER ISOLATION | 01-0.75"-INA1483-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1919 | PD-559
01-VINA175 | END USER ISOLATION | 01-0.75"-INA1377-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1920 | PD-559
01-VINA176 | END USER ISOLATION | 01-0.75"-INA1378-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1921 | PD-559
01-VINA177 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1050-1DCD1A-1.0 "EOI | 0.75" | Globe valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 1922 | PD-552
01-VINA178 | END USER ISOLATION | 01-0.75"-INA1380-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1923 | PD-559
01-VINA179 | DRAIN | 01-0.75"-INA1090-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1924 | PD-552
01-VINA180 | DRAIN | 01-0.75"-INA1064-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1925 | PD-552
01-VINA181 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1050-1DCD1A-1.0 "EOI | 0.75" | Y stop check valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 1926 | PD-552
01-VINA182 | END USER ISOLATION | 01-0.75"-INA1384-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1927 | PD-559
01-VINA183 | STUB-UP ISOLATION | 01-1"-INA1068-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1928 | PD-557
01-VINA184 | STUB-UP ISOLATION | 01-1"-INA1461-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1929 | PD-557
01-VINA185 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-0.75"-INA1050-1DCD1A-1.0 "EOI | 0.75" | Check valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 1930 | PD-552
01-VINA186 | STUB-UP ISOLATION | 00-1"-INA1661-1KFB1A | 1" | Ball valve | INA | 1KFB1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1931 | PD-557
01-VINA187 | DRAIN | 01-0.75"-INA1686-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1932 | PD-557
01-VINA188 | END USER ISOLATION | 01-0.75"-INA1141-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1933 | PD-557
01-VINA189 | DRAIN | 01-0.75"-INA1010-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1934 | PD-557
01-VINA190 | STUB-UP ISOLATION | 01-2"-INA1018-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1935 | PD-557
01-VINA191 | DRAIN | 01-0.75"-INA1076-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1936 | PD-559
01-VINA192 | STUB-UP ISOLATION | 01-0.75"-INA1034-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1937 | PD-552
01-VINA193 | STUB-UP ISOLATION | 01-1"-INA1045-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1938 | PD-557
01-VINA194 | DRAIN | 01-0.75"-INA1454-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1939 | PD-558
01-VINA195 | STUB-UP ISOLATION | 01-2"-INA1016-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1940 | PD-557
01-VINA196 | STUB-UP ISOLATION | 01-0.75"-INA1022-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1941 | PD-557
01-VINA197 | END USER ISOLATION | 01-0.75"-INA1398-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1942 | PD-558
01-VINA198 | DRAIN | 01-0.75"-INA1461-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1943 | PD-557
01-VINA199 | STUB-UP ISOLATION | 01-1"-INA1028-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1944 | PD-557
01-VINA200 | END USER ISOLATION | 01-0.75"-INA1401-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1945 | PD-559
01-VINA201 | END USER ISOLATION | 01-0.75"-INA1402-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1946 | PD-559
01-VINA202 | DRAIN | 01-0.75"-INA1454-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1947 | PD-558
01-VINA203 | DRAIN | 01-0.75"-INA1076-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1948 | PD-557
01-VINA204 | DRAIN | 01-0.75"-INA1249-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1949 | PD-552
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 1950 | P&ID
01-VINA205 | END USER ISOLATION | 01-0.75"-INA1406-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1951 | PD-559
01-VINA206 | END USER ISOLATION | 01-1.5"-INA1031-1KFD1A | 1.5" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1952 | PD-559
01-VINA207 | END USER ISOLATION | 01-0.75"-INA1399-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1953 | PD-559
01-VINA208 | END USER ISOLATION | 01-0.75"-INA1409-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1954 | PD-559
01-VINA209 | END USER ISOLATION | 01-0.75"-INA1408-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1955 | PD-559
01-VINA210 | END USER ISOLATION | 01-0.75"-INA1411-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1956 | PD-559
01-VINA211 | END USER ISOLATION | 01-0.75"-INA1093-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1957 | PD-559
01-VINA212 | END USER ISOLATION | 01-0.75"-INA1312-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1958 | PD-559
01-VINA213 | STUB-UP ISOLATION | 01-1"-INA1026-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1959 | PD-557
01-VINA214 | DRAIN | 01-0.75"-INA1659-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1960 | PD-557
01-VINA215 | END USER ISOLATION | 01-0.75"-INA1004-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1961 | PD-559
01-VINA216 | DRAIN | 01-0.75"-INA1477-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1962 | PD-559
01-VINA217 | DRAIN | 01-0.75"-INA1460-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1963 | PD-557
01-VINA218 | STUB-UP ISOLATION | 01-1"-INA1076-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1964 | PD-557
01-VINA219 | END USER ISOLATION | 01-0.75"-INA1140-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1965 | PD-557
01-VINA220 | DRAIN | 01-0.75"-INA1011-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1966 | PD-557
01-VINA221 | STUB-UP ISOLATION | 01-2"-INA1023-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1967 | PD-557
01-VINA222 | STUB-UP ISOLATION | 01-2"-INA1098-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1968 | PD-557
01-VINA223 | STUB-UP ISOLATION | 01-1.5"-INA1096-1KFD1A | 1.5" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1969 | PD-557
01-VINA224 | STUB-UP ISOLATION | 01-1"-INA1027-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1970 | PD-557
01-VINA225 | DRAIN | 01-0.75"-INA1140-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1971 | PD-557
01-VINA226 | END USER ISOLATION | 01-0.75"-INA1242-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1972 | PD-558
01-VINA227 | END USER ISOLATION | 01-0.75"-INA1003-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1973 | PD-559
01-VINA228 | END USER ISOLATION | 01-0.75"-INA1410-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1974 | PD-559
01-VINA229 | END USER ISOLATION | 01-0.75"-INA1407-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1975 | PD-559
01-VINA230 | END USER ISOLATION | 01-0.75"-INA1405-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1976 | PD-559
01-VINA231 | DRAIN | 01-0.75"-INA1140-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1977 | PD-557
01-VINA232 | END USER ISOLATION | 01-0.75"-INA1403-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1978 | PD-559
01-VINA233 | END USER ISOLATION | 01-0.75"-INA1375-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1979 | PD-560
01-VINA234 | DRAIN | 01-0.75"-INA1068-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1980 | PD-557
01-VINA235 | END USER ISOLATION | 01-0.75"-INA1315-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1981 | PD-560
01-VINA236 | END USER ISOLATION | 01-0.75"-INA1331-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1982 | PD-560
01-VINA237 | END USER ISOLATION | 01-0.75"-INA1332-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1983 | PD-560
01-VINA238 | END USER ISOLATION | 01-0.75"-INA1353-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1984 | PD-558
01-VINA239 | END USER ISOLATION | 01-0.75"-INA1001-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1985 | PD-560
01-VINA240 | END USER ISOLATION | 01-0.75"-INA1351-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1986 | PD-560
01-VINA241 | END USER ISOLATION | 01-0.75"-INA1340-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1987 | PD-560
01-VINA242 | END USER ISOLATION | 01-0.75"-INA1349-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1988 | PD-560
01-VINA243 | END USER ISOLATION | 01-0.75"-INA1348-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1989 | PD-558
01-VINA244 | END USER ISOLATION | 01-0.75"-INA1347-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1990 | PD-558
01-VINA245 | END USER ISOLATION | 01-1"-INA1688-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1991 | PD-558
01-VINA246 | END USER ISOLATION | 01-0.75"-INA1345-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1992 | PD-560
01-VINA248 | END USER ISOLATION | 01-0.75"-INA1659-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1993 | PD-557
01-VINA251 | END USER ISOLATION | 01-0.75"-INA1010-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1994 | PD-557
01-VINA254 | END USER ISOLATION | 01-0.75"-INA1011-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1995 | PD-557
01-VINA258 | DRAIN | 01-0.75"-INA1068-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1996 | PD-557
01-VINA259 | END USER ISOLATION | 01-0.75"-INA1002-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1997 | PD-552
01-VINA260 | END USER ISOLATION | 01-0.75"-INA1020-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1998 | PD-552
01-VINA261 | END USER ISOLATION | 01-0.75"-INA1021-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 1999 | PD-552
01-VINA262 | END USER ISOLATION | 01-0.75"-INA1024-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2000 | PD-552
01-VINA263 | END USER ISOLATION | 01-0.75"-INA1032-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2001 | PD-552
01-VINA264 | END USER ISOLATION | 01-0.75"-INA1034-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2002 | PD-552
01-VINA266 | DRAIN | 01-0.75"-INA1471-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2003 | PD-558
01-VINA267 | END USER ISOLATION | 01-0.75"-INA1035-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2004 | PD-552
01-VINA268 | END USER ISOLATION | 01-0.75"-INA1036-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2005 | PD-552
01-VINA269 | DRAIN | 01-0.75"-INA1469-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2006 | PD-558
01-VINA270 | DRAIN | 01-0.75"-INA1476-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2007 | PD-558
01-VINA271 | DRAIN | 01-0.75"-INA1476-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2008 | PD-558
01-VINA272 | END USER ISOLATION | 01-1"-INA1311-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2009 | PD-558
01-VINA273 | END USER ISOLATION | 01-0.75"-INA1104-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2010 | PD-552
01-VINA274 | END USER ISOLATION | 01-0.75"-INA1102-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2011 | PD-552
01-VINA275 | DRAIN | 01-0.75"-INA1236-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2012 | PD-558
01-VINA276 | END USER ISOLATION | 01-0.75"-INA1236-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2013 | PD-558
01-VINA277 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-1"-INA1109-1ECD1A-1.0 "EOI | 1" | Y stop check valve | INA | 1ECD1A | AIR | CL800 | SWE | SWE | 682 | 482 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 2014 | PD-552
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2015 | P&ID
01-VINA278 | AIR SUPPLY OVERPRESSURE PROTECTION | 01-1"-INA1109-1ECD1A-1.0 "EOI | 1" | Check valve | INA | 1ECD1A | AIR | CL800 | SWE | SWE | 682 | 482 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 2016 | PD-552
01-VINA280 | END USER ISOLATION | 01-0.75"-INA1105-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2017 | PD-552
01-VINA281 | DRAIN | 01-0.75"-INA1659-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2018 | PD-557
01-VINA282 | DRAIN | 01-0.75"-INA1072-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2019 | PD-557
01-VINA283 | DRAIN | 01-0.75"-INA1030-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2020 | PD-557
01-VINA284 | DRAIN | 01-0.75"-INA1029-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2021 | PD-557
01-VINA285 | DRAIN | 01-0.75"-INA1680-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2022 | PD-557
01-VINA286 | DRAIN | 01-0.75"-INA1028-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2023 | PD-557
01-VINA287 | END USER ISOLATION | 01-0.75"-INA1234-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2024 | PD-559
01-VINA288 | DRAIN | 01-0.75"-INA1076-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2025 | PD-557
01-VINA289 | DRAIN | 01-0.75"-INA1027-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2026 | PD-557
01-VINA290 | DRAIN | 01-0.75"-INA1037-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2027 | PD-557
01-VINA291 | DRAIN | 01-0.75"-INA1026-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2028 | PD-557
01-VINA292 | DRAIN | 01-0.75"-INA1080-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2029 | PD-557
01-VINA294 | DRAIN | 01-0.75"-INA1230-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2030 | PD-552
01-VINA295 | DRAIN | 01-0.75"-INA1086-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2031 | PD-552
01-VINA296 | END USER ISOLATION | 01-0.75"-INA1224-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2032 | PD-552
01-VINA297 | DRAIN | 01-0.75"-INA1006-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2033 | PD-552
01-VINA298 | DRAIN | 01-0.75"-INA1002-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2034 | PD-552
01-VINA299 | DRAIN | 01-0.75"-INA1020-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2035 | PD-552
01-VINA300 | END USER ISOLATION | 01-0.75"-INA1344-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2036 | PD-560
01-VINA301 | END USER ISOLATION | 01-0.75"-INA1355-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2037 | PD-560
01-VINA302 | END USER ISOLATION | 01-0.75"-INA1336-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2038 | PD-560
01-VINA303 | END USER ISOLATION | 01-0.75"-INA1350-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2039 | PD-560
01-VINA304 | END USER ISOLATION | 01-0.75"-INA1000-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2040 | PD-560
01-VINA305 | END USER ISOLATION | 01-0.75"-INA1352-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2041 | PD-560
01-VINA307 | END USER ISOLATION | 01-0.75"-INA1337-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2042 | PD-560
01-VINA308 | END USER ISOLATION | 01-0.75"-INA1343-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2043 | PD-560
01-VINA309 | END USER ISOLATION | 01-0.75"-INA1338-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2044 | PD-560
01-VINA310 | DRAIN | 01-0.75"-INA1021-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2045 | PD-552
01-VINA311 | END USER ISOLATION | 01-0.75"-INA1342-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2046 | PD-560
01-VINA312 | END USER ISOLATION | 01-0.75"-INA1354-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2047 | PD-560
01-VINA313 | END USER ISOLATION | 01-0.75"-INA1339-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2048 | PD-560
01-VINA314 | END USER ISOLATION | 01-0.75"-INA1232-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2049 | PD-558
01-VINA315 | DRAIN | 01-0.75"-INA1232-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2050 | PD-558
01-VINA316 | END USER ISOLATION | 01-0.75"-INA1229-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2051 | PD-558
01-VINA317 | DRAIN | 01-0.75"-INA1024-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2052 | PD-552
01-VINA318 | DRAIN | 01-0.75"-INA1038-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2053 | PD-552
01-VINA319 | END USER ISOLATION | 01-0.75"-INA1227-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2054 | PD-558
01-VINA320 | DRAIN | 01-0.75"-INA1226-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2055 | PD-552
01-VINA321 | DRAIN | 01-0.75"-INA1127-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2056 | PD-552
01-VINA322 | DRAIN | 01-0.75"-INA1476-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2057 | PD-558
01-VINA323 | END USER ISOLATION | 01-0.75"-INA1220-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2058 | PD-558
01-VINA324 | DRAIN | 01-0.75"-INA1478-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2059 | PD-558
01-VINA325 | END USER ISOLATION | 01-0.75"-INA1219-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2060 | PD-558
01-VINA326 | DRAIN | 01-0.75"-INA1478-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2061 | PD-558
01-VINA327 | DRAIN | 01-0.75"-INA1470-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2062 | PD-558
01-VINA328 | DRAIN | 01-0.75"-INA1481-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2063 | PD-558
01-VINA329 | DRAIN | 01-0.75"-INA1481-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2064 | PD-558
01-VINA330 | DRAIN | 01-0.75"-INA1304-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2065 | PD-558
01-VINA331 | DRAIN | 01-0.75"-INA1348-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2066 | PD-558
01-VINA332 | END USER ISOLATION | 01-1"-INA1278-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2067 | PD-558
01-VINA333 | DRAIN | 01-0.75"-INA1311-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2068 | PD-558
01-VINA334 | END USER ISOLATION | 01-1"-INA1153-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2069 | PD-558
01-VINA335 | DRAIN | 01-0.75"-INA1278-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2070 | PD-558
01-VINA336 | DRAIN | 01-0.75"-INA1311-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2071 | PD-558
01-VINA337 | END USER ISOLATION | 01-0.75"-INA1276-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2072 | PD-560
01-VINA338 | DRAIN | 01-0.75"-INA1347-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2073 | PD-558
01-VINA339 | DRAIN | 01-0.75"-INA1278-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2074 | PD-558
01-VINA340 | END USER ISOLATION | 01-0.75"-INA1275-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2075 | PD-560
01-VINA341 | DRAIN | 01-0.75"-INA1353-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2076 | PD-558
01-VINA342 | DRAIN | 01-0.75"-INA1153-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2077 | PD-558
01-VINA343 | END USER ISOLATION | 01-0.75"-INA1244-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2078 | PD-558
01-VINA344 | DRAIN | 01-0.75"-INA1688-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2079 | PD-558
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2080 | P&ID
01-VINA345 | END USER ISOLATION | 01-1"-INA1150-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2081 | PD-558
01-VINA346 | END USER ISOLATION | 01-0.75"-INA1396-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2082 | PD-558
01-VINA347 | END USER ISOLATION | 01-0.75"-INA1397-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2083 | PD-558
01-VINA348 | END USER ISOLATION | 01-0.75"-INA1687-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2084 | PD-558
01-VINA349 | END USER ISOLATION | 01-0.75"-INA1478-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2085 | PD-558
01-VINA350 | END USER ISOLATION | 01-0.75"-INA1480-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2086 | PD-558
01-VINA351 | END USER ISOLATION | 01-0.75"-INA1476-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2087 | PD-558
01-VINA352 | DRAIN | 01-0.75"-INA1150-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2088 | PD-558
01-VINA353 | DRAIN | 01-0.75"-INA1219-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2089 | PD-558
01-VINA354 | DRAIN | 01-0.75"-INA1220-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2090 | PD-558
01-VINA355 | DRAIN | 01-0.75"-INA1220-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2091 | PD-558
01-VINA356 | DRAIN | 01-0.75"-INA1277-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2092 | PD-558
01-VINA357 | DRAIN | 01-0.75"-INA1040-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2093 | PD-558
01-VINA358 | DRAIN | 01-0.75"-INA1040-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2094 | PD-558
01-VINA359 | DRAIN | 01-0.75"-INA1277-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2095 | PD-558
01-VINA360 | DRAIN | 01-0.75"-INA1277-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2096 | PD-558
01-VINA361 | DRAIN | 01-0.75"-INA1277-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2097 | PD-558
01-VINA362 | DRAIN | 01-0.75"-INA1396-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2098 | PD-558
01-VINA363 | DRAIN | 01-0.75"-INA1397-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2099 | PD-558
01-VINA364 | DRAIN | 01-0.75"-INA1490-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2100 | PD-558
01-VINA365 | DRAIN | 01-0.75"-INA1249-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2101 | PD-552
01-VINA366 | DRAIN | 01-0.75"-INA1248-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2102 | PD-552
01-VINA367 | END USER ISOLATION | 01-0.75"-INA1057-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2103 | PD-559
01-VINA368 | END USER ISOLATION | 01-0.75"-INA1247-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2104 | PD-552
01-VINA369 | END USER ISOLATION | 01-0.75"-INA1058-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2105 | PD-559
01-VINA370 | END USER ISOLATION | 01-0.75"-INA1114-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2106 | PD-552
01-VINA371 | DRAIN | 01-0.75"-INA1058-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2107 | PD-559
01-VINA372 | END USER ISOLATION | 01-0.75"-INA1226-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2108 | PD-552
01-VINA373 | END USER ISOLATION | 01-0.75"-INA1480-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2109 | PD-558
01-VINA374 | DRAIN | 01-0.75"-INA1456-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2110 | PD-559
01-VINA376 | DRAIN | 01-0.75"-INA1234-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2111 | PD-559
01-VINA377 | DRAIN | 01-0.75"-INA1479-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2112 | PD-559
01-VINA379 | END USER ISOLATION | 01-1"-INA1304-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2113 | PD-558
01-VINA381 | END USER ISOLATION | 01-0.75"-INA1230-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2114 | PD-552
01-VINA383 | DRAIN | 01-0.75"-INA1057-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2115 | PD-559
01-VINA384 | DRAIN | 01-0.75"-INA1077-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2116 | PD-559
01-VINA385 | DRAIN | 01-0.75"-INA1329-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2117 | PD-559
01-VINA386 | DRAIN | 01-0.75"-INA1327-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2118 | PD-559
01-VINA387 | DRAIN | 01-0.75"-INA1312-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2119 | PD-559
01-VINA388 | DRAIN | 01-0.75"-INA1328-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2120 | PD-559
01-VINA389 | DRAIN | 01-0.75"-INA1313-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2121 | PD-559
01-VINA390 | DRAIN | 01-0.75"-INA1019-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2122 | PD-559
01-VINA391 | DRAIN | 01-0.75"-INA1380-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2123 | PD-559
01-VINA392 | DRAIN | 01-0.75"-INA1380-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2124 | PD-559
01-VINA393 | DRAIN | 01-0.75"-INA1401-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2125 | PD-559
01-VINA394 | DRAIN | 01-0.75"-INA1378-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2126 | PD-559
01-VINA396 | DRAIN | 01-0.75"-INA1377-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2127 | PD-559
01-VINA397 | DRAIN | 01-1"-INA1474-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2128 | PD-559
01-VINA399 | DRAIN | 01-1"-INA1094-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2129 | PD-559
01-VINA400 | END USER ISOLATION | 01-0.75"-INA1488-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2130 | PD-558
01-VINA401 | END USER ISOLATION | 01-0.75"-INA1489-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2131 | PD-558
01-VINA402 | END USER ISOLATION | 01-0.75"-INA1490-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2132 | PD-558
01-VINA410 | END USER ISOLATION | 01-1"-INA1092-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2133 | PD-552
01-VINA411 | END USER ISOLATION | 01-0.75"-INA1064-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2134 | PD-552
01-VINA412 | END USER ISOLATION | 01-1"-INA1121-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2135 | PD-552
01-VINA413 | END USER ISOLATION | 01-1"-INA1007-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2136 | PD-552
01-VINA414 | END USER ISOLATION | 01-0.75"-INA1008-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2137 | PD-552
01-VINA415 | STUB-UP ISOLATION | 01-1"-INA1007-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2138 | PD-552
01-VINA416 | DRAIN | 01-1"-INA1094-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2139 | PD-559
01-VINA417 | STUB-UP ISOLATION | 01-1"-INA1030-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2140 | PD-557
01-VINA418 | END USER ISOLATION | 01-0.75"-INA1680-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2141 | PD-557
01-VINA419 | END USER ISOLATION | 01-0.75"-INA1066-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2142 | PD-557
01-VINA420 | END USER ISOLATION | 01-0.75"-INA1037-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2143 | PD-557
01-VINA421 | END USER ISOLATION | 01-0.75"-INA1081-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2144 | PD-557
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2145 | P&ID
01-VINA422 | END USER ISOLATION | 01-0.75"-INA1080-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2146 | PD-557
01-VINA424 | DRAIN | 01-0.75"-INA1250-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2147 | PD-559
01-VINA425 | DRAIN | 01-0.75"-INA1333-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2148 | PD-559
01-VINA426 | DRAIN | 01-0.75"-INA1334-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2149 | PD-559
01-VINA428 | DRAIN | 01-0.75"-INA1403-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2150 | PD-559
01-VINA429 | END USER ISOLATION | 01-0.75"-INA1516-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2151 | PD-559
01-VINA430 | DRAIN | 01-0.75"-INA1516-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2152 | PD-559
01-VINA431 | DRAIN | 01-0.75"-INA1405-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2153 | PD-559
01-VINA432 | DRAIN | 01-0.75"-INA1399-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2154 | PD-559
01-VINA433 | DRAIN | 01-0.75"-INA1400-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2155 | PD-559
01-VINA434 | DRAIN | 01-0.75"-INA1395-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2156 | PD-559
01-VINA435 | DRAIN | 01-0.75"-INA1098-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2157 | PD-560
01-VINA436 | DRAIN | 01-0.75"-INA1314-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2158 | PD-560
01-VINA438 | DRAIN | 01-0.75"-INA1315-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2159 | PD-560
01-VINA439 | DRAIN | 01-0.75"-INA1341-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2160 | PD-560
01-VINA440 | DRAIN | 01-0.75"-INA1331-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2161 | PD-560
01-VINA441 | DRAIN | 01-0.75"-INA1332-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2162 | PD-560
01-VINA442 | DRAIN | 01-0.75"-INA1340-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2163 | PD-560
01-VINA443 | DRAIN | 01-0.75"-INA1001-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2164 | PD-560
01-VINA445 | DRAIN | 01-0.75"-INA1351-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2165 | PD-560
01-VINA446 | DRAIN | 01-0.75"-INA1345-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2166 | PD-560
01-VINA447 | DRAIN | 01-0.75"-INA1492-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2167 | PD-560
01-VINA448 | DRAIN | 01-0.75"-INA1350-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2168 | PD-560
01-VINA450 | DRAIN | 01-0.75"-INA1352-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2169 | PD-560
01-VINA451 | DRAIN | 01-0.75"-INA1000-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2170 | PD-560
01-VINA452 | DRAIN | 01-0.75"-INA1336-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2171 | PD-560
01-VINA453 | DRAIN | 01-0.75"-INA1355-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2172 | PD-560
01-VINA454 | DRAIN | 01-0.75"-INA1344-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2173 | PD-560
01-VINA455 | DRAIN | 01-0.75"-INA1343-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2174 | PD-560
01-VINA456 | DRAIN | 01-0.75"-INA1338-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2175 | PD-560
01-VINA457 | DRAIN | 01-0.75"-INA1342-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2176 | PD-560
01-VINA458 | DRAIN | 01-0.75"-INA1354-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2177 | PD-560
01-VINA459 | DRAIN | 01-0.75"-INA1339-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2178 | PD-560
01-VINA460 | END USER ISOLATION | 01-0.75"-INA1341-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2179 | PD-560
01-VINA461 | DRAIN | 01-0.75"-INA1102-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2180 | PD-552
01-VINA462 | END USER ISOLATION | 01-0.75"-INA1115-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2181 | PD-552
01-VINA463 | DRAIN | 01-0.75"-INA1232-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2182 | PD-558
01-VINA464 | STUB-UP ISOLATION | 01-2"-INA1277-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2183 | PD-552
01-VINA469 | DRAIN | 01-0.75"-INA1349-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2184 | PD-560
01-VINA470 | DRAIN | 01-0.75"-INA1695-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2185 | PD-552
01-VINA475 | DRAIN | 01-0.75"-INA1219-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2186 | PD-552
01-VINA476 | DRAIN | 01-0.75"-INA1219-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2187 | PD-552
01-VINA479 | END USER ISOLATION | 01-0.75"-INA1492-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2188 | PD-560
01-VINA480 | END USER ISOLATION | 01-0.75"-INA1491-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2189 | PD-560
01-VINA500 | DRAIN | 01-0.75"-INA1232-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2190 | PD-558
01-VINA515 | DRAIN | 01-0.75"-INA1229-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2191 | PD-558
01-VINA545 | DRAIN | 01-0.75"-INA1082-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 2192 | PD-552
01-VLPS101 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-1"-LPS1408-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2193 | PD-040A
01-VLPS102 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1409-1DAA1A-2.0 "EIC | 0.75" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2194 | PD-040A
01-VLPS103 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-1"-LPS1409-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2195 | PD-040A
01-VLPS104 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-1"-LPS1410-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2196 | PD-040A
01-VLPS106 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-1"-LPS1411-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2197 | PD-040A
01-VLPS107 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1411-1DAA1A-2.0 "EIC | 0.75" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2198 | PD-040A
01-VLPS108 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-2"-LPS1400-1DAA1A-2.0 "EIC | 2" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | VALVE TO BE FULL PORT (I.E. 100% BORE AREA) | 2199 | PD-040A
01-VLPS109 | DRIP LEG DRAIN | 01-2"-LPS1401-1DAA1A-2.0 "EIC | 2" | Ball valve | LPS | 1DAA1A | Steam | CL600 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 2200 | PD-040A
01-VLPS111 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-2"-LPS1400-1DAA1A-2.0 "EIC | 2" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | VALVE TO BE FULL PORT (I.E. 100% BORE AREA) | 2201 | PD-040A
01-VLPS112 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1465-1DAA1A-1.5 "EOC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 2202 | PD-040A
01-VLPS123 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1465-1DAA1A-1.5 "EOC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 2203 | PD-040A
01-VLPS142 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1466-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2204 | PD-040A
01-VLPS147 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1473-1BAA1A-1.5 "EOH | 0.75" | Globe valve | LPS | 1BAA1A | Steam | CL1500 | SWE | SWE | 50 | 624 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 2205 | PD-041A
01-VLPS149 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-2"-LPS1413-1DAA1A-2.0 "EIC | 2" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2206 | PD-041A
01-VLPS150 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-2"-LPS1413-1DAA1A-2.0 "EIC | 2" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2207 | PD-041A
01-VLPS151 | DRIP LEG DRAIN | 01-2"-LPS1429-1DAA1A-2.0 "EIC | 2" | Ball valve | LPS | 1DAA1A | Steam | CL600 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 2208 | PD-041A
01-VLPS152 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1463-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2209 | PD-040A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2210 | P&ID
01-VLPS161 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1473-1BAA1A-1.5 "EOH | 0.75" | Globe valve | LPS | 1BAA1A | Steam | CL1500 | SWE | SWE | 50 | 624 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 2211 | PD-041A
01-VLPS163 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1466-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2212 | PD-041A
01-VLPS164 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1463-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2213 | PD-040A
01-VLPS167 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1466-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2214 | PD-040A
01-VLPS169 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-1"-LPS1405-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2215 | PD-041A
01-VLPS170 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-1"-LPS1406-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2216 | PD-041A
01-VLPS171 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-1"-LPS1407-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2217 | PD-041A
01-VLPS172 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-1"-LPS1404-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2218 | PD-041A
01-VLPS173 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1466-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2219 | PD-041A
01-VLPS175 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1405-1DAA1A-2.0 "EIC | 0.75" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2220 | PD-041A
01-VLPS177 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 01-0.75"-LPS1407-1DAA1A-2.0 "EIC | 0.75" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 2221 | PD-041A
01-VPDR100 | TRANSFORMER CONTAINMENT ISOLATION | 01-4"-PDR0143-1ADA2U | 4" | Gate valve | PDR | 1ADA2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 2222 | PD-970
01-VPDR101 | TRANSFORMER CONTAINMENT ISOLATION | 01-4"-PDR0145-1ADA2U | 4" | Gate valve | PDR | 1ADA2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 2223 | PD-970
01-VPDR105 | OWS INLET ISOLATION | 01-12"-PDR0101-1ADA2U | 12" | Gate valve | PDR | 1ADA2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 2224 | PD-960A
01-VPDR107 | TRENCH DRAIN CHECK/FLAPPER VALVE | 01-12"-PDR0153-1ADA1U | 12" | Check valve | PDR | 1ADA1U | OIL/WATER | CL150 | NONE/INLINE | INTERNAL CLAMP | 0 | 200 | S-SV |  | No | 94.03.56.100.1 | TIDEFLEX CHECKMATE OR EQUIV., RUBBER INLINE CHECK VALVE, PIPE ID: 11.94 +/- 0.19 IN, MATERIALS SUITABLE FOR OILY WATER WORKING FLUID | 2225 | PD-972
01-VPDR108 | TRENCH DRAIN CHECK/FLAPPER VALVE | 01-4"-PDR0157-1ADA1U | 4" | Check valve | PDR | 1ADA1U | OIL/WATER | CL150 | NONE/INLINE | INTERNAL CLAMP | 0 | 200 | S-SV |  | No | 94.03.56.100.1 | TIDEFLEX CHECKMATE OR EQUIV., RUBBER INLINE CHECK VALVE, PIPE ID: 3.94 +/- 0.09 IN, MATERIALS SUITABLE FOR OILY WATER WORKING FLUID | 2226 | PD-972
01-VPDR109 | TRENCH DRAIN CHECK/FLAPPER VALVE | 01-12"-PDR0162-1ADA1U | 12" | Check valve | PDR | 1ADA1U | OIL/WATER | CL150 | NONE/INLINE | INTERNAL CLAMP | 0 | 200 | S-SV |  | No | 94.03.56.100.1 | TIDEFLEX CHECKMATE OR EQUIV., RUBBER INLINE CHECK VALVE, PIPE ID: 11.94 +/- 0.19 IN, MATERIALS SUITABLE FOR OILY WATER WORKING FLUID | 2227 | PD-972
01-VSMP100 | UNIT 1 SAMPLE PANEL HP BLOWDOWN HEADER DRAIN ISOLATION VALVE | 01-0.75"-SMP1011-1DCA3A-2.5 "EOH | 0.75" | Gate valve | SMP | 1DCA3A | Water | CL600 | SWE | SWE | 15 | 1097 | S-40S | 2.5 " | Yes | 94.03.68.150.02.2H |  | 2228 | PD-500A
01-VSTP100 | HP CONTROL VALVE HP STEM LEAK CHECK VALVE | 01-1.5"-STP1060-1GBB1A-3.5 "EIC | 1.5" | Check valve | STP | 1GBB1A | Steam/Water | CL1500 | SWE | SWE | 630 | 1073 | S-160 | 3.5 " | No | 94.03.68.150.02.1H | PISTON LIFT | 2229 | PD-303A
01-VSTP101 | HP STOP VALVE HP STEM LEAK CHECK VALVE | 01-1.5"-STP1041-1GBB1A-3.5 "EIC | 1.5" | Check valve | STP | 1GBB1A | Steam/Water | CL1500 | SWE | SWE | 630 | 1073 | S-160 | 3.5 " | No | 94.03.68.150.02.1H | PISTON LIFT | 2230 | PD-303A
01-VSTP102 | HP STEM LEAK TO CRH CHECK VALVE | 01-2"-STP1041-1GBB1A-4.0 "EIC | 2" | Check valve | STP | 1GBB1A | Steam/Water | CL1500 | SWE | SWE | 630 | 1073 | S-160 | 4.0 " | No | 94.03.68.150.02.1H | PISTON LIFT | 2231 | PD-303A
01-VSTP103 | HP STEM LEAK TO HP DRN TANK CHECK VALVE | 01-2"-STP1043-1GBB1A-4.0 "EIC | 2" | Check valve | STP | 1GBB1A | Steam/Water | CL1500 | SWE | SWE | 630 | 1073 | S-160 | 4.0 " | No | 94.03.68.150.02.1H | PISTON LIFT | 2232 | PD-303A
01-VSTP104 | HP STEAM INLET PIPE DRAIN MANUAL ISOLATION | 01-1.5"-STP1089-1HBD1A-3.5 "EIC | 1.5" | Gate valve | STP | 1HBD1A | Steam/Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 3.5 " | No | 94.03.68.150.02.1H | RATED FOR VACUUM SERVICE | 2233 | PD-303A
01-VSTP105 | CMV SEAT DRAIN MANUAL ISOLATION | 01-1.5"-STP1020-1HBD1A-3.5 "EIC | 1.5" | Gate valve | STP | 1HBD1A | Steam/Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 3.5 " | No | 94.03.68.150.02.1H |  | 2234 | PD-303A
01-VSTP106 | IP STEAM INLET PIPE DRAIN MANUAL ISOLATION | 01-1"-STP1064-1FBD1A-3.5 "EIC | 1" | Gate valve | STP | 1FBD1A | Steam/Water | CL1500 | SWE | SWE | 624 | 1096 | S-80 | 3.5 " | No | 94.03.68.150.02.1H | RATED FOR VACUUM SERVICE | 2235 | PD-303A
01-VSTP107 | CRV SEAT DRAIN MANUAL ISOLATION | 01-1"-STP1066-1FBD1A-3.5 "EIC | 1" | Gate valve | STP | 1FBD1A | Steam/Water | CL1500 | SWE | SWE | 624 | 1096 | S-80 | 3.5 " | No | 94.03.68.150.02.1H |  | 2236 | PD-303A
01-VSTP108 | LP STEAM STRAINER DRAIN MANUAL ISOLATION | 01-1"-STP1068-1DAA1A-2.0 "EIC | 1" | Gate valve | STP | 1DAA1A | Steam/Water | CL800 | SWE | SWE | 131 | 697 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 2237 | PD-303A
01-VSTP109 | LP STEAM INLET PIPE DRAIN MANUAL ISOLATION | 01-1"-STP1069-1DAA1A-2.0 "EIC | 1" | Gate valve | STP | 1DAA1A | Steam/Water | CL800 | SWE | SWE | 131 | 697 | S-80 | 2.0 " | No | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2238 | PD-303A
01-VSTP110 | INSTRUMENT | 01-0.75"-STP1014-1BAB1A-1.5 "EOC | 0.75" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 2239 | PD-304A
01-VSTP111 | INSTRUMENT | 01-2"-STP1016-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 2240 | PD-304A
01-VSTP112 | INSTRUMENT | 01-2"-STP1017-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 2241 | PD-304A
01-VSTP113 | HP ST DRAINS TANK DRAIN ISOLATION | 01-6"-STP1006-1BAA1A-1.0 "MOH | 6" | Gate valve | STP | 1BAA1A | Water | CL150 | RFFE | RFFE | 50 | 240 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | FLEXIBLE WEDGE | 2242 | PD-304A
01-VSTP114 | DRAIN | 01-0.75"-STP1006-1BAA1A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA1A | Water | CL800 | SWE | SWE | 50 | 240 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2243 | PD-304A
01-VSTP115 | HP ST DRAINS TANK DRAIN ISOLATION | 01-6"-STP1018-1BCA2A-1.0 "MOH | 6" | Gate valve | STP | 1BCA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE, TWO PHASE FLOW, 6% STEAM FLASHING | 2244 | PD-304A
01-VSTP116 | DRAIN | 01-2"-STP1019-1BAB1A-1.5 "EOH | 2" | Gate valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 2245 | PD-304A
01-VSTP117 | GLAND STEAM CONDENSER DRAIN ISOLATION | 01-0.75"-STP1075-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | VACUUM SERVICE | 2246 | PD-306A
01-VSTP118 | DRAIN | 01-0.75"-STP1048-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | VACUUM SERVICE | 2247 | PD-306A
01-VSTP119 | GSC EMERGENCY LOOP SEAL DRAIN ISOLATION | 01-2"-STP1045-1BAA1A-1.0 "MIC | 2" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2248 | PD-302A
01-VSTP120 | GLAND STEAM CONDENSER STEAM TRAP DRAIN ISOLATION | 01-2"-STP1053-1BAA1A-1.0 "MIC | 2" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2249 | PD-302A
01-VSTP121 | GLAND STEAM CONDENSER STEAM TRAP DRAIN ISOLATION | 01-2"-STP1053-1BAA1A-1.0 "MIC | 2" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2250 | PD-302A
01-VSTP122 | GLAND STEAM CONDENSER STEAM TRAP STRAINER DRAIN ISOLATION | 01-1"-STP1053-1BAA1A-1.0 "MIC | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2251 | PD-302A
01-VSTP123 | GLAND STEAM CONDENSER STEAM TRAP BYPASS THROTTLIING | 01-2"-STP1116-1BAA1A-1.0 "MIC | 2" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2252 | PD-302A
01-VSTP124 | DRAIN | 01-0.75"-STP1103-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | VACUUM SERVICE | 2253 | PD-306A
01-VSTP125 | GSC FAN EXHAUST CHECK VALVE | 01-6"-STP1027-1BAA2A-1.0 "MIC | 6" | Check valve | STP | 1BAA2A | AIR | CL150 | WAFER | WAFER | 15 | 212 | S-40 | 1.0 " | No | 94.03.68.150.03.2H | DUAL PLATE CHECK VALVE, FLOW- 250 SCFM (FlUID- AIR), CRACKING PRESSURE <0.075 PSID IN VERTICAL (FLOW UP) ORIENTATION | 2254 | PD-302A
01-VSTP126 | VENT | 01-0.75"-STP1104-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2255 | PD-306A
01-VSTP127 | GLAND STEAM SPILLOVER CONTROL VALVE ISOLATION | 01-8"-STP1065-1DAA1A-3.0 "EIC | 8" | Gate valve | STP | 1DAA1A | Steam | CL300 | RFFE | RFFE | 100 | 797 | S-40 | 3.0 " | No | 94.03.68.150.03.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN, VACUUM SERVICE | 2256 | PD-300A
01-VSTP128 | GSC FAN EXHAUST CHECK VALVE | 01-6"-STP1026-1BAA2A-1.0 "MIC | 6" | Check valve | STP | 1BAA2A | AIR | CL150 | WAFER | WAFER | 15 | 212 | S-40 | 1.0 " | No | 94.03.68.150.03.2H | DUAL PLATE CHECK VALVE, FLOW- 250 SCFM (FlUID- AIR), CRACKING PRESSURE <0.075 PSID IN VERTICAL (FLOW UP) ORIENTATION | 2257 | PD-302A
01-VSTP129 | GLAND STEAM SPILLOVER CONTROL VALVE ISOLATION | 01-12"-STP1065-1DAA1A-3.5 "EIC | 12" | Gate valve | STP | 1DAA1A | Steam | CL300 | RFFE | RFFE | 100 | 797 | S-STD | 3.5 " | No | 94.03.68.150.03.2H | DOUBLE DISC WEDGE, 3-WAY DRAIN, VACUUM SERVICE | 2258 | PD-300A
01-VSTP130 | DRAIN | 01-0.75"-STP1003-1BAA1A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA1A | Water | CL800 | SWE | SWE | 50 | 240 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2259 | PD-304A
01-VSTP131 | INSTRUMENT | 01-1"-STP1655-1DAA1A-2.0 "EIC | 1" | Globe valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H |  | 2260 | PD-300A
01-VSTP132 | GLAND STEAM SPILLOVER CONTROL VALVE BYPASS | 01-6"-STP1653-1DAA1A-3.0 "EIC | 6" | Globe valve | STP | 1DAA1A | Steam | CL300 | RFFE | RFFE | 100 | 797 | S-40 | 3.0 " | No | 94.03.68.150.06.1H | VACUUM SERVICE, THROTTLING, GEAR OPERATOR | 2261 | PD-300A
01-VSTP133 | INSTRUMENT | 01-1"-STP1655-1DAA1A-2.0 "EIC | 1" | Globe valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H |  | 2262 | PD-300A
01-VSTP134 | INSTRUMENT | 01-2"-STP1001-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 2263 | PD-304A
01-VSTP135 | INSTRUMENT | 01-2"-STP1005-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 2264 | PD-304A
01-VSTP136 | INSTRUMENT | 01-0.75"-STP1052-1BAB1A-1.5 "EOC | 0.75" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 2265 | PD-304A
01-VSTP137 | GLAND STEAM CONDENSER STEAM TRAP EQUALIZING ISOLATION | 01-1"-STP1067-1BAA1A-1.0 "MIC | 1" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2266 | PD-302A
01-VSTP138 | DRAIN ISOLATION | 01-1"-STP1015-1BAA1A-2.0 "EII | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.3H |  | 2267 | PD-300A
01-VSTP139 | DRAIN ISOLATION | 01-1"-STP1062-1BAA1A-2.0 "EIC | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 797 | S-80 | 2.0 " | No | 94.03.68.150.02.3H |  | 2268 | PD-302A
01-VSTP140 | DRAIN ISOLATION | 01-1"-STP1054-1DBB1A-3.5 "EIC | 1" | Gate valve | STP | 1DBB1A | Steam/Water | CL800 | SWE | SWE | 15 | 1076 | S-80 | 3.5 " | No | 94.03.68.150.02.3H |  | 2269 | PD-302A
01-VSTP141 | INSTRUMENT | 01-0.75"-STP1149-1BAB1A-1.0 "MOC | 0.75" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | No | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2270 | PD-305A
01-VSTP142 | INSTRUMENT | 01-0.75"-STP1189-1BAB1A-1.0 "MOC | 0.75" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | No | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2271 | PD-305A
01-VSTP143 | INSTRUMENT | 01-2"-STP1091-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2272 | PD-305A
01-VSTP144 | INSTRUMENT | 01-2"-STP1097-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2273 | PD-305A
01-VSTP145 | DRAIN ISOLATION | 01-1"-STP1039-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2274 | PD-302A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2275 | P&ID
01-VSTP146 | DRAIN ISOLATION | 01-1"-STP1023-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2276 | PD-302A
01-VSTP147 | DRAIN ISOLATION | 01-1"-STP1033-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2277 | PD-302A
01-VSTP148 | INSTRUMENT | 01-2"-STP1074-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2278 | PD-305A
01-VSTP149 | INSTRUMENT | 01-2"-STP1072-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2279 | PD-305A
01-VSTP150 | INSTRUMENT | 01-2"-STP1098-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2280 | PD-305A
01-VSTP151 | INSTRUMENT | 01-2"-STP1099-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2281 | PD-305A
01-VSTP152 | DRAIN | 01-2"-STP1209-1BAB1A-1.0 "MOH | 2" | Gate valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2282 | PD-305A
01-VSTP153 | DRAIN ISOLATION | 01-1"-STP1024-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2283 | PD-302A
01-VSTP154 | LP STEAM DRAINS PUMP A SUCTION ISOLATION | 01-1"-STP1049-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2284 | PD-302A
01-VSTP155 | INSTRUMENT | 01-0.75"-STP1106-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2285 | PD-306A
01-VSTP156 | INSTRUMENT | 01-0.75"-STP1107-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2286 | PD-306A
01-VSTP157 | VENT | 01-0.75"-STP1081-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2287 | PD-306A
01-VSTP158 | DRAIN | 01-0.75"-STP1108-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2288 | PD-306A
01-VSTP159 | GLAND STEAM MIST SEPARATOR DRAIN ISOLATION | 01-1"-STP1008-1BAA1A-1.0 "EIC | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 100 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2289 | PD-300A
01-VSTP160 | INSTRUMENT | 01-0.75"-STP1102-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2290 | PD-306A
01-VSTP161 | LP STEAM DRAINS PUMP A VENT ISOLATION | 01-0.75"-STP1071-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2291 | PD-306A
01-VSTP162 | INSTRUMENT | 01-0.75"-STP1085-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2292 | PD-306A
01-VSTP163 | LP STEAM DRAINS PUMP A DISCHARGE CHECK VALVE | 01-6"-STP1085-1BAA2A-1.0 "MOH | 6" | Check valve | STP | 1BAA2A | Water | CL150 | RFFE | RFFE | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, SWING CHECK, VERTICAL INSTALLATION, MAX FLOW- 700 GPM, MIN FLOW- 450 GPM | 2293 | PD-306A
01-VSTP164 | DRAIN | 01-0.75"-STP1085-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2294 | PD-306A
01-VSTP165 | LP STEAM DRAINS PUMP A DISCHARGE ISOLATION | 01-6"-STP1085-1BAA2A-1.0 "MOH | 6" | Gate valve | STP | 1BAA2A | Water | CL150 | RFFE | RFFE | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE | 2295 | PD-306A
01-VSTP166 | VENT | 01-0.75"-STP1085-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2296 | PD-306A
01-VSTP167 | GLAND STEAM MIST SEPARATOR DRAIN ORIFICE BYPASS | 01-1"-STP1115-1BAA1A-1.0 "EIC | 1" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 100 | 392 | S-80 | 1.0 " | No | 94.03.68.150.02.3H | RATED FOR VACUUM SERVICE | 2297 | PD-300A
01-VSTP168 | INSTRUMENT | 01-0.75"-STP1109-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2298 | PD-306A
01-VSTP169 | INSTRUMENT | 01-0.75"-STP1110-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2299 | PD-306A
01-VSTP170 | VENT | 01-0.75"-STP1083-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2300 | PD-306A
01-VSTP171 | DRAIN | 01-0.75"-STP1114-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2301 | PD-306A
01-VSTP172 | PRIMING CONNECTION ISOLATION | 01-0.75"-STP1054-1DBB1A-3.0 "EIC | 0.75" | Gate valve | STP | 1DBB1A | Steam/Water | CL800 | SWE | SWE | 15 | 1076 | S-80 | 3.0 " | No | 94.03.68.150.02.1H |  | 2302 | PD-302A
01-VSTP173 | INSTRUMENT | 01-0.75"-STP1105-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2303 | PD-306A
01-VSTP174 | LP STEAM DRAINS PUMP B VENT ISOLATION | 01-0.75"-STP1073-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2304 | PD-306A
01-VSTP175 | INSTRUMENT | 01-0.75"-STP1084-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2305 | PD-306A
01-VSTP176 | LP STEAM DRAINS PUMP B DISCHARGE CHECK VALVE | 01-6"-STP1084-1BAA2A-1.0 "MOH | 6" | Check valve | STP | 1BAA2A | Water | CL150 | RFFE | RFFE | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, SWING CHECK, VERTICAL INSTALLATION, MAX FLOW- 700 GPM, MIN FLOW- 450 GPM | 2306 | PD-306A
01-VSTP177 | DRAIN | 01-0.75"-STP1084-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 2307 | PD-306A
01-VSTP178 | LP STEAM DRAINS PUMP B DISCHARGE ISOLATION | 01-6"-STP1084-1BAA2A-1.0 "MOH | 6" | Gate valve | STP | 1BAA2A | Water | CL150 | RFFE | RFFE | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE | 2308 | PD-306A
01-VSTP179 | GSC FAN EXHAUST ISOLATION | 01-6"-STP1026-1BAA2A-1.0 "MIC | 6" | Butterfly valve | STP | 1BAA2A | AIR | CL150 | LUGGED | LUGGED | 15 | 212 | S-40 | 1.0 " | No | 94.03.68.150.04.1 |  | 2309 | PD-302A
01-VSTP180 | GSC FAN EXHAUST ISOLATION | 01-6"-STP1027-1BAA2A-1.0 "MIC | 6" | Butterfly valve | STP | 1BAA2A | AIR | CL150 | LUGGED | LUGGED | 15 | 212 | S-40 | 1.0 " | No | 94.03.68.150.04.1 |  | 2310 | PD-302A
01-VSTP181 | GLAND STEAM MIST SEPARATOR DRAIN THROTTLE | 01-1"-STP1008-1BAA1A-1.0 "EIC | 1" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 100 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2311 | PD-300A
01-VSTP182 | GLAND STEAM MIST SEPARATOR DRAIN ISOLATION | 01-1"-STP1008-1BAA1A-1.0 "EIC | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 100 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2312 | PD-300A
01-VSTP183 | GLAND STEAM HEADER DRAIN ISOLATION | 01-1"-STP1032-1DAA1A-2.0 "EIC | 1" | Gate valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2313 | PD-300A
01-VSTP184 | GLAND STEAM HEADER DRAIN THROTTLE | 01-1"-STP1032-1DAA1A-2.0 "EIC | 1" | Globe valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2314 | PD-300A
01-VSTP185 | GLAND STEAM HEADER DRAIN ISOLATION | 01-1"-STP1032-1DAA1A-2.0 "EIC | 1" | Gate valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 2315 | PD-300A
01-VSTP195 | INSTRUMENT | 01-2"-STP1100-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 2316 | PD-304A
01-VSTP196 | INSTRUMENT | 01-2"-STP1101-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 2317 | PD-304A
01-VSTP370 | HP ST DRAINS TANK DRAIN ISOLATION | 01-6"-STP1002-1BCA2A-1.0 "MOH | 6" | Gate valve | STP | 1BCA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE, TWO PHASE FLOW, 6% STEAM FLASHING | 2318 | PD-304A
01-VSTP371 | HP ST DRAINS TANK DRAIN ISOLATION | 01-6"-STP1003-1BAA1A-1.0 "MOH | 6" | Gate valve | STP | 1BAA1A | Water | CL150 | RFFE | RFFE | 50 | 240 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | FLEXIBLE WEDGE | 2319 | PD-304A
01-VSTP386 | CONDENSATE RECEIVER TANK ISOLATION | 01-6"-STP1085-1BAA2A-1.0 "MOH | 6" | Butterfly valve | STP | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 | RATED FOR VACUUM SERVICE | 2320 | PD-306A
01-VSWS100 | BEARING FLUSH ISOLATION | 01-1"-SWS1031-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2321 | PD-090A
01-VSWS101 | INSTRUMENTATION | 01-0.5"-SWS1192-1BAB3A-1.0 "MOH | 0.5" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2322 | PD-090A
01-VSWS102 | INSTRUMENTATION | 01-0.5"-SWS1192-1BAB3A-1.0 "MOH | 0.5" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2323 | PD-090A
01-VSWS103 | VACUUM PUMP MAKEUP ISOLATION | 01-1"-SWS1022-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2324 | PD-395
01-VSWS104 | VACUUM PUMP MAKEUP ISOLATION | 01-1"-SWS1021-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2325 | PD-395
01-VSWS105 | VACUUM PUMP MAKEUP ISOLATION | 01-1"-SWS1020-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2326 | PD-395
01-VSWS106 | FIN TUBE CLEANING SKID ISOLATION | 01-2"-SWS1180-1BAH1A-1.0 "MOH | 2" | Ball valve | SWS | 1BAH1A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2327 | PD-395
01-VSWS108 | DRAIN | 01-0.75"-SWS1192-1BAB3A-1.0 "MOH | 0.75" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2328 | PD-090A
01-VSWS109 | UNIT 1 HRSG BLOWDOWN SUMP QUENCH ISOLATION | 01-3"-SWS1016-1BAH1A-1.0 "MOH | 3" | Ball valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.03.0 |  | 2329 | PD-090A
01-VSWS110 | DRAIN | 01-0.75"-SWS1016-1BAB3A-1.0 "MOH | 0.75" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2330 | PD-090A
01-VSWS111 | UNIT 1 HRSG BLOWDOWN TANK/SUMP QUENCH ISOLATION | 01-6"-SWS1192-1BAH1A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 2331 | PD-090A
01-VSWS115 | VACUUM PUMP MAKEUP ISOLATION | 01-1"-SWS1015-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2332 | PD-395
01-VSWS118 | VACUUM PUMP MAKEUP ISOLATION | 01-1"-SWS1018-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2333 | PD-395
01-VWDR100 | OIL IN WATER ANALYZER ISOLATION VALVE | 01-0.75"-WDR1179-1BAB2A-1.0 "MOH | 0.75" | Globe valve | WDR | 1BAB2A | Water | CL800 | SWE | SWE | 50 | 200 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 2334 | PD-960A
01-VWDR137 | VENT | 01-0.75"-WDR1179-1BAB2A-1.0 "MOH | 0.75" | Globe valve | WDR | 1BAB2A | Water | CL800 | SWE | SWE | 50 | 200 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2335 | PD-960A
01-YV-BFW309 | TCA COOLER INLET EMERGENCY SHUTOFF | 01-6"-BFW1028-1HAC2A-1.5 "EOH | 6" | Globe control valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.5 " | Yes | 94.03.68.100.01.2 |  | 2336 | PD-063A
01-YV-BFW319 | CTA COOLER BFW SUPPLY STARTUP VALVE | 01-1"-BFW1377-1HAC2A-1.0 "EOH | 1" | Globe control valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 2337 | PD-063A
01-YV-BFW409 | FGH UPSTREAM BFW EMERGENCY SHUTOFF | 01-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.100.01.2 |  | 2338 | PD-064A
01-YV-BFW419 | FG HX BFW SUPPLY STARTUP VALVE | 01-1"-BFW1454-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 2339 | PD-064A
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2340 | P&ID
01-YV-BFW445 | FGH BFW OUTLET EMERGENCY SHUTOFF | 01-4"-BFW1008-1FAC1A-1.0 "EOH | 4" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 2341 | PD-064A
01-YV-BFW705 | HPS TA SPRAY SUPPLY AUTOMATIC BLOCK | 01-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Globe control valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.100.01.0 |  | 2342 | PD-020A
01-YV-BFW715 | HPS BYPASS SPRAY SUPPLY AUTOMATIC BLOCK | 01-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.100.01.0 |  | 2343 | PD-020A
01-YV-BFW735 | HRH SPRAY SUPPLY AUTOMATIC BLOCK | 01-3"-BFW1108-1FAC1A-1.0 "EOH | 3" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.100.01.0 |  | 2344 | PD-034A
01-YV-BFW745 | CRH LETDOWN PCV SPRAY AUTOMATIC BLOCK | 01-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 2345 | PD-124A
01-YV-BFW757 | CRH LETDOWN ATTEMPERATOR SPRAY AUTOMATIC BLOCK | 01-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 2346 | PD-124A
01-YV-CND441 | CND SYSTEM EMERGENCY DUMP VALVE | 01-3"-CND1103-1EAA2A-1.0 "MOH | 3" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 2347 | PD-053A
01-YV-CND509 | ECA COOLER LOOP SUPPLY AUTOMATIC ISOLATION | 01-6"-CND1031-1EAA1A-1.0 "EOH | 6" | Globe control valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.100.02.2 | ON/OFF SOLENOID, OPEN AND CLOSED LIMIT SWITCHES, FAIL OPEN | 2348 | PD-054A
01-YV-CND571 | ECA COOLER LOOP RETURN AUTOMATIC ISOLATION | 01-6"-CND1039-1EAA1A-1.0 "EOH | 6" | Globe control valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.100.02.2 | ON/OFF SOLENOID, OPEN AND CLOSED LIMIT SWITCHES, FAIL OPEN | 2349 | PD-054A
01-YV-CND702 | HRH BYPASS SPRAY SUPPLY AUTOMATIC BLOCK | 01-4"-CND1256-1EAA2A-1.0 "MIC | 4" | Globe control valve | CND | 1EAA2A | Water | CL600 | RFFE | RFFE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.100.01.0 |  | 2350 | PD-034A
01-YV-CND705 | CRH VENTILATOR SPRAY AUTOMATIC BLOCK | 01-3"-CND1062-1EAA2A-1.0 "MIC | 3" | Globe control valve | CND | 1EAA2A | Water | CL600 | RFFE | RFFE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.100.01.3 |  | 2351 | PD-030A
01-YV-CND721 | GLAND STEAM DSH SPRAY SUPPLY AUTOMATIC BLOCK | 01-1"-CND1181-1EAA2A-1.0 "MIC | 1" | Globe control valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.100.02.2 |  | 2352 | PD-300A
01-YV-CND725 | LP BYPASS VALVE SPRAY SUPPLY AUTOMATIC BLOCK | 01-1"-CND1459-1EAA2A-1.0 "MIC | 1" | Globe control valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.100.01.0 |  | 2353 | PD-040A
01-YV-DWS719 | CONDENSER EMERGENCY MAKEUP ON/OFF | 01-6"-DWS1006-1BCA2A-1.0 "MOH | 6" | Butterfly control valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 2354 | PD-050A
01-YV-STP131 | HP ST DRAINS TANK DRAIN ON/OFF | 01-6"-STP1018-1BCA2A-1.0 "MOH | 6" | Globe control valve | STP | 1BCA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-10S | 1.0 " | Yes | 94.03.68.100.02.3 | RATED FOR VACCUM SERVICE, LESS THAN 5 SEC TO ACTUATE, SEE VALVE DATASHEET FOR MORE DETAILS | 2355 | PD-304A
01-YV-STP132 | HP ST DRAINS TANK DRAIN ON/OFF | 01-6"-STP1002-1BCA2A-1.0 "MOH | 6" | Globe control valve | STP | 1BCA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-10S | 1.0 " | Yes | 94.03.68.100.02.3 | RATED FOR VACCUM SERVICE, LESS THAN 5 SEC TO ACTUATE, SEE VALVE DATASHEET FOR MORE DETAILS | 2356 | PD-304A
01-YV-WDR110 | UNIT 1 OWS AUTOMATIC ISOLATION VALVE | 01-6"-WDR1179-1BAB2A-1.0 "MOH | 6" | Butterfly control valve | WDR | 1BAB2A | Water | CL150 | RFFE | RFFE | 50 | 200 | S-40 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 2357 | PD-960A
02-FCV-BFW147 | BFP A MIN RECIRC CV | 02-3"-BFW1066-1HBB1A-1.0 "EOH | 3" | Angle globe control valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.100.02.0 |  | 2358 | PD-061B
02-FCV-BFW187 | BFP B MIN RECIRC CV | 02-3"-BFW1074-1HBB1A-1.0 "EOH | 3" | Angle globe control valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.100.02.0 |  | 2359 | PD-061B
02-FCV-BFW343 | CT TCA COOLER BFW TCV TO HRSG | 02-4"-BFW1324-1HBB1A-2.0 "EOH | 4" | Angle globe control valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.0 " | Yes | 94.03.68.100.02.0 |  | 2360 | PD-063B
02-FCV-BFW359 | CT TCA COOLER BFW TCV RECIRC TO ACC | 02-3"-BFW1426-1HBB1A-2.0 "EOH | 3" | Angle globe control valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.0 " | Yes | 94.03.68.100.02.0 |  | 2361 | PD-063B
02-FCV-BFW459 | FG HX BFW FCV TO LP ECON | 02-2"-BFW1008-1FAC1A-1.0 "EOH | 2" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.100.02.0 |  | 2362 | PD-064B
02-FCV-BFW475 | FG HX BFW FCV RECIRC TO ACC | 02-2"-BFW1093-1FBB1A-1.0 "EOH | 2" | Globe control valve | BFW | 1FBB1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.100.02.0 |  | 2363 | PD-064B
02-FCV-CND331 | CONDENSATE MINIMUM RECIRC VALVE | 02-6"-CND1161-1EAA2A-1.0 "MOH | 6" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.100.02.0 |  | 2364 | PD-053B
02-LCV-DWS715 | CONDENSER MAKEUP LEVEL CONTROL | 02-2"-DWS1017-1BCA2A-1.0 "MOH | 2" | Globe control valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.100.02.3 |  | 2365 | PD-050B
02-LV-CRH109 | DRIP LEG DRAIN - AUTOMATED | 02-2"-CRH1025-1EBB1A-3.5 "EIC | 2" | Ball control valve | CRH | 1EBB1A | Steam | CL600 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 2366 | PD-030B
02-LV-CRH110 | DRIP LEG DRAIN - AUTOMATED | 02-2"-CRH1026-1EBA1A-2.0 "EOH | 2" | Ball control valve | CRH | 1EBA1A | Steam | CL600 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 2367 | PD-030B
02-LV-CRH125 | DRIP LEG DRAIN - AUTOMATED | 02-2"-CRH1004-1EBA1A-2.0 "EOH | 2" | Ball control valve | CRH | 1EBA1A | Steam | CL600 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 2368 | PD-031B
02-LV-LPS115 | DRIP LEG DRAIN - AUTOMATED | 02-2"-LPS1401-1DAA1A-2.0 "EIC | 2" | Ball control valve | LPS | 1DAA1A | Steam | CL600 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 2369 | PD-040B
02-LV-LPS123 | DRIP LEG DRAIN - AUTOMATED | 02-2"-LPS1429-1DAA1A-2.0 "EIC | 2" | Ball control valve | LPS | 1DAA1A | Steam | CL600 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 2370 | PD-041B
02-MOV-AXS321 | UNIT 1 ISOLATION | 02-6"-AXS1500-1DAA1A-1.5 "EOC | 6" | Control valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.150.03.0 | MOTOR OPERATOR, FLEXIBLE WEDGE, 3-WAY DRAIN W/ LOW PRESSURE SIDE MOTOR OPERATED VALVE, LIMIT SWITCHES | 2371 | PD-123B
02-MOV-BFW139 | BFP A IP DISCHARGE ISOLATION MOV | 02-6"-BFW1374-1FAC1A-1.5 "EOH | 6" | Control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0 | PARALLEL SLIDE DISC, 3-WAY DRAIN WITH LOW PRESSURE SIDE MOTOR OPERATED VALVE | 2372 | PD-060B
02-MOV-BFW145 | BFP A HP DISCHARGE ISOLATION MOV | 02-10"-BFW1029-1HAC2A-1.5 "EOH | 10" | Control valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0 | PARALLEL SLIDE DISC, 3-WAY DRAIN WITH LOW PRESSURE SIDE MOTOR OPERATED VALVE | 2373 | PD-061B
02-MOV-BFW179 | BFP B IP DISCHARGE ISOLATION MOV | 02-6"-BFW1063-1FAC1A-1.5 "EOH | 6" | Control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0 | PARALLEL SLIDE DISC, 3-WAY DRAIN WITH LOW PRESSURE SIDE MOTOR OPERATED VALVE | 2374 | PD-060B
02-MOV-BFW185 | BFP B HP DISCHARGE ISOLATION MOV | 02-10"-BFW1052-1HAC2A-1.5 "EOH | 10" | Control valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0 | PARALLEL SLIDE DISC, 3-WAY DRAIN WITH LOW PRESSURE SIDE MOTOR OPERATED VALVE | 2375 | PD-061B
02-MOV-CND201 | CONDENSATE IRON FILTER AUTOMATIC ISOLATION | 02-12"-CND1037-1EAA2A-1.0 "MOH | 12" | Control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1 | PARALLEL SLIDE DISC, MOTOR OPERATOR | 2376 | PD-052B
02-MOV-CND211 | CONDENSATE IRON FILTER AUTOMATIC ISOLATION | 02-12"-CND1027-1EAA2A-1.0 "MOH | 12" | Control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1 | PARALLEL SLIDE DISC, MOTOR OPERATOR | 2377 | PD-052B
02-MOV-CND221 | CONDENSATE IRON FILTER AUTOMATIC BYPASS | 02-12"-CND1088-1EAA2A-1.0 "MOH | 12" | Control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1 | FLEXIBLE WEDGE, MOTOR OPERATOR | 2378 | PD-052B
02-PCV-AXS713 | DA EJECTOR STEAM SUPPLY CONTROL VALVE | 02-1"-AXS1508-1DAA1A-1.0 "EOC | 1" | Globe control valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.100.02.1 | HYDRO VALVE KIT | 2379 | PD-050B
02-PCV-CCW191 | SYSTEM BALANCING CONTROL VALVE | 02-10"-CCW1141-1BAB2A | 10" | Ball control valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.100.02.3 |  | 2380 | PD-270B
02-PCV-CMG117 | CO2 BACKPRESSURE REGULATOR | 02-2"-CMG1010-1BCB6A | 2" | Self contained backpress reg | CMG | 1BCB6A | CARBON DIOXIDE | CL600 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.100.02.2 |  | 2381 | PD-571
02-PCV-CND289 | ACC DUCT CURTAIN SPRAY CONTROL VALVE | 02-2.5"-CND1038-1EAA2A-1.0 "MIC | 2.5" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.100.02.1 |  | 2382 | PD-052B
02-PCV-CND423 | CND LP ECON AND DRUM BYPASS CONTROL VALVE | 02-6"-CND1020-1EAA2A-1.0 "MOH | 6" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.100.02.0 |  | 2383 | PD-053B
02-PCV-CND455 | LP ECONOMIZER INLET PCV | 02-8"-CND1187-1EAA2A-1.0 "MOH | 8" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 2384 | PD-053B
02-PCV-CRH700 | CRH TO AXS PRESSURE LETDOWN (LOW FLOW) | 02-2"-CRH1193-1EBA1A-2.5 "EOC | 2" | Globe control valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-80 | 2.5 " | No | 94.03.68.100.01.2 | - | 2385 | PD-124B
02-PCV-CRH715 | CRH TO AXS PRESSURE LETDOWN (HIGH FLOW) | 02-6"-CRH1162-1EBA1A-3.0 "EOC | 6" | Globe control valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 3.0 " | No | 94.03.68.100.01.2 | - | 2386 | PD-124B
02-PCV-HPS100 | HPS BYPASS VALVE | 02-10"-HPS1175-1HBD2A-6.0 "EOC | 10" | Steam Bypass Valve | HPS | 1HBD2A | Steam | CL2500 SPL | BE | BE | 2534 | 1097 | 1.171" min | 6.0 " | No | 94.03.68.100.01.0 |  | 2387 | PD-020B
02-PCV-HRH100 | BYPASS VALVE | 02-24"-HRH1265-1FBD1A-7.0 "EIC | 24" | Angle control valve | HRH | 1FBD1A | Steam | CL600 SPL | BE | BE | 586 | 1096 | S-60 | 7.0 " | No | 94.03.68.100.01.0 | - | 2388 | PD-034B
02-PCV-LPS100 | BYPASS VALVE | 02-12"-LPS1453-1DAA1A-3.0 "EIC | 12" | Angle control valve | LPS | 1DAA1A | Steam | CL150 | BE | BE | 119 | 624 | S-STD | 3.0 " | No | 94.03.68.100.01.0 | - | 2389 | PD-040B
02-PRV-CMG101 | NITROGEN STORAGE CYLINDER RACK OUTLET | 02-1"-CMG1101-1BCA1A | 1" | Self contained press red reg | CMG | 1BCA1A | NITROGEN | CL600 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.100.02.2 |  | 2390 | PD-570
02-PRV-CMG102 | NITROGEN STORAGE CYLINDER RACK OUTLET | 02-1"-CMG1102-1BCA1A | 1" | Self contained press red reg | CMG | 1BCA1A | NITROGEN | CL600 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.100.02.2 |  | 2391 | PD-570
02-PRV-CMG115 | CO2 PRESSURE REGULATOR | 02-2"-CMG1011-1BCB6A-1.0 "MOH | 2" | Self contained backpress reg | CMG | 1BCB6A | CARBON DIOXIDE | CL600 | SWE | SWE | 200 | 115 | S-40S | 1.0 " | Yes | 94.03.68.100.02.3 |  | 2392 | PD-571
02-PRV-CND325 | STEAM DRAINS PUMP SEAL WATER PRV | 02-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Self contained press red reg | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.3 |  | 2393 | PD-306B
02-PRV-CND326 | STEAM DRAINS PUMP SEAL WATER PRV | 02-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Self contained press red reg | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.3 |  | 2394 | PD-306B
02-PRV-CTP112 | EVAP COOLER PRESSURE REGULATOR | 02-3"-CTP1060-1BCA2A-1.0 "MOH | 3" | Self contained press red reg | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 2395 | PD-333B
02-PRV-SWS713 | BEARING FLUSH PRESSURE REGULATOR | 02-1"-SWS1031-1BAB3A-1.0 "MOH | 1" | Self contained press red reg | SWS | 1BAB3A | Water | CL600 | FTE | FTE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 2396 | PD-090B
02-PSV-AXS325 | STEAM HEADER SAFETY VALVE | 02-4"-AXS1934-1DAA1A-1.5 "EOC | 4" | Angle press relief valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.175.0 |  | 2397 | PD-123B
02-PSV-AXS329 | HEAT EXCHANGER RELIEF VALVE | 02-0.75"-AXS1042-1DAA1A-1.0 "EOC | 0.75" | Angle press relief valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.175.0 |  | 2398 | PD-123B
02-PSV-AXS391 | SAFTEY VALVE AT HRSG CONNECTIONS | 02-1"-AXS1258-1DAA1A-1.0 "EOH | 1" | Angle press relief valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2399 | PD-122B
02-PSV-BFW104 | BFP SUCTION HEADER PSV | 02-4"-BFW1096-1DAA1A-1.0 "EOH | 4" | Angle press relief valve | BFW | 1DAA1A | Water | CL300 | RFFE | RFFE | 300 | 360 | S-40 | 1.0 " | Yes | 94.03.68.175.0 |  | 2400 | PD-060B
02-PSV-BFW105 | BFP A SUCTION OVERPRESSURE PROTECTION | 02-1.5"-BFW1024-1DAA1A-1.0 "EOH | 1.5" | Angle press relief valve | BFW | 1DAA1A | Water | CL300 | RFFE | RFFE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2401 | PD-060B
02-PSV-BFW155 | BFP B SUCTION OVERPRESSURE PROTECTION | 02-1.5"-BFW1022-1DAA1A-1.0 "EOH | 1.5" | Angle press relief valve | BFW | 1DAA1A | Water | CL300 | RFFE | RFFE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2402 | PD-060B
02-PSV-BFW323 | CT TCA COOLER OVERPRESSURE PROTECTION | 02-1"-BFW1318-1HAC2A-1.0 "EOH | 1" | Angle press relief valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.175.0 |  | 2403 | PD-063B
02-PSV-BFW423 | FG HX OVERPRESSURE PROTECTION | 02-0.75"-BFW1483-1FAC1A-1.0 "EOH | 0.75" | Angle press relief valve | BFW | 1FAC1A | Water | CL900 | SWE | RFFE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2404 | PD-064B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2405 | P&ID
02-PSV-BFW463 | FG STARTUP HEATER PSV | 02-0.75"-BFW1106-1FAC1A-1.0 "EOH | 0.75" | Angle press relief valve | BFW | 1FAC1A | Water | CL900 | SWE | RFFE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2406 | PD-064B
02-PSV-BFW751 | FG HX OUTLET CND RETURN PSV | 02-1.5"-BFW1146-1EAA1A-1.0 "EOH | 1.5" | Angle press relief valve | BFW | 1EAA1A | Water | CL600 | BE | RFFE | 790 | 589 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2407 | PD-053B
02-PSV-CCW213 | RELIEF VALVE | 02-0.75"-CCW1166-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 2408 | PD-271B
02-PSV-CCW223 | RELIEF VALVE | 02-0.75"-CCW1104-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 2409 | PD-271B
02-PSV-CCW233 | RELIEF VALVE | 02-0.75"-CCW1169-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 2410 | PD-271B
02-PSV-CCW243 | RELIEF VALVE | 02-0.75"-CCW1107-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 2411 | PD-271B
02-PSV-CCW253 | RELIEF VALVE | 02-0.75"-CCW1181-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-80 |  | No | 94.03.68.175.0 |  | 2412 | PD-271B
02-PSV-CCW311 | RELIEF VALVE | 02-0.75"-CCW1207-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2413 | PD-272B
02-PSV-CCW331 | RELIEF VALVE | 02-0.75"-CCW1221-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2414 | PD-272B
02-PSV-CCW351 | RELIEF VALVE | 02-0.75"-CCW1241-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2415 | PD-272B
02-PSV-CCW381 | RELIEF VALVE | 02-0.75"-CCW1321-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2416 | PD-273B
02-PSV-CCW391 | RELIEF VALVE | 02-0.75"-CCW1309-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2417 | PD-273B
02-PSV-CCW413 | RELIEF VALVE | 02-0.75"-CCW1089-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2418 | PD-274B
02-PSV-CCW423 | RELIEF VALVE | 02-0.75"-CCW1088-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2419 | PD-274B
02-PSV-CCW433 | RELIEF VALVE | 02-0.75"-CCW1087-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2420 | PD-274B
02-PSV-CCW443 | RELIEF VALVE | 02-0.75"-CCW1086-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2421 | PD-274B
02-PSV-CCW453 | RELIEF VALVE | 02-0.75"-CCW1085-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2422 | PD-274B
02-PSV-CCW463 | RELIEF VALVE | 02-0.75"-CCW1084-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2423 | PD-274B
02-PSV-CCW473 | RELIEF VALVE | 02-0.75"-CCW1083-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2424 | PD-274B
02-PSV-CCW483 | RELIEF VALVE | 02-0.75"-CCW1082-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2425 | PD-274B
02-PSV-CCW511 | RELIEF VALVE | 02-0.75"-CCW1080-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2426 | PD-275B
02-PSV-CCW531 | RELIEF VALVE | 02-0.75"-CCW1090-1BAB2A | 0.75" | Angle press relief valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-80 |  | No | 94.03.68.175.0 |  | 2427 | PD-275B
02-PSV-CMG116 | NITROGEN OVERPRESSURE PROTECTION | 02-1"-CMG1116-1BCA1A | 1" | Angle press relief valve | CMG | 1BCA1A | NITROGEN | CL150 | RFFE | RFFE | 130 | 115 | S-40S |  | No | 94.03.68.175.2 |  | 2428 | PD-570
02-PSV-CMG118 | CO2 OVERPRESSURE PROTECTION | 02-1"-CMG1018-1BCB6A | 1" | Angle press relief valve | CMG | 1BCB6A | CARBON DIOXIDE | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.175.2 |  | 2429 | PD-571
02-PSV-CMG126 | NITROGEN OVERPRESSURE PROTECTION | 02-1"-CMG1126-1BCA1A | 1" | Angle press relief valve | CMG | 1BCA1A | NITROGEN | CL150 | RFFE | RFFE | 130 | 115 | S-40S |  | No | 94.03.68.175.2 |  | 2430 | PD-570
02-PSV-CND101 | CND PUMP A SUCTION OVERPRESSURE PROTECTION | 02-0.75"-CND1011-1BAA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1BAA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2431 | PD-051B
02-PSV-CND121 | CND PUMP B SUCTION OVERPRESSURE PROTECTION | 02-0.75"-CND1019-1BAA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1BAA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2432 | PD-051B
02-PSV-CND141 | CND PUMP C SUCTION OVERPRESSURE PROTECTION | 02-0.75"-CND1013-1BAA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1BAA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2433 | PD-051B
02-PSV-CND255 | DWS TO CND PSV | 02-0.75"-CND1111-1BCA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1BCA2A | Water | CL150 | SWE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.175.0 |  | 2434 | PD-052B
02-PSV-CND402 | CONDENSATE FILL TO HP BFW OVERPRESSURE PROTECTION | 02-0.75"-CND1156-1EAA2A-1.0 "MOH | 0.75" | Angle control valve | CND | 1EAA2A | Water | CL600 | SWE | RFFE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2435 | PD-061B
02-PSV-CND403 | CONDENSATE FILL TO IP BFW OVERPRESSURE PROTECTION | 02-0.75"-CND1003-1EAA2A-1.0 "MOH | 0.75" | Angle press relief valve | CND | 1EAA2A | Water | CL600 | SWE | RFFE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2436 | PD-062B
02-PSV-CND457 | LP ECONOMIZER INLET OVERPRESSURE PROTECTION | 02-4"-CND1687-1DAA2A-1.0 "MOH | 4" | Angle press relief valve | CND | 1DAA2A | Water | CL300 | RFFE | RFFE | 600 | 290 | S-40 | 1.0 " | Yes | 94.03.68.175.0 |  | 2437 | PD-053B
02-PSV-CND519 | ECA COOLER THERMAL RELIEF OVERPRESSURE PROTECTION | 02-1"-CND1221-1EAA1A-1.0 "EOH | 1" | Angle press relief valve | CND | 1EAA1A | Water | CL600 | RFFE | RFFE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.175.0 |  | 2438 | PD-054B
02-PSV-CTP118 | EVAP COOLER OVERPRESSURE PROTECTION | 02-1"-CTP1010-1BCA2A-1.0 "MOH | 1" | Angle control valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.175.1 |  | 2439 | PD-333B
02-PSV-CTP128 | CT CASING COOLING AIR PIPING PSV | 02-0.75"-CTP1020-1BCA2A | 0.75" | Angle press relief valve | CTP | 1BCA2A | AIR | CL150 | RFFE | RFFE | 145 | 212 | S-40S |  | No | 94.03.68.175.2 |  | 2440 | PD-336B
02-PSV-FGS159 | PERFORMANCE HEATER PSV | 02-1"-FGS1036-1EAL1A-1.0 "EOC | 1" | Angle press relief valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.175.1 |  | 2441 | PD-656B
02-PSV-INA100 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1043-1BCD2A | 0.75" | Angle press relief valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-40S |  | No | 94.03.68.175.2 |  | 2442 | PD-562
02-PSV-INA101 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1047-1BCD2A | 0.75" | Angle press relief valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-40S |  | No | 94.03.68.175.2 |  | 2443 | PD-562
02-PSV-INA104 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1084-1BCD2A | 0.75" | Angle press relief valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-40S |  | No | 94.03.68.175.2 |  | 2444 | PD-558
02-PSV-INA105 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1106-1BCD2A | 0.75" | Angle press relief valve | INA | 1BCD2A | AIR | CL150 | RFFE | RFFE | 145 | 140 | S-40S |  | No | 94.03.68.175.2 |  | 2445 | PD-562
02-PSV-STP209 | GLAND STEAM PSV | 02-3"-STP1004-1DAA1A-2.5 "EIC | 3" | Angle press relief valve | STP | 1DAA1A | Steam | CL300 | RFFE | RFFE | 100 | 797 | S-40 | 2.5 " | No | 94.03.68.175.1 |  | 2446 | PD-300B
02-TCV-AXS371 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE | 02-1"-AXS1505-1DCA1A-1.0 "EOH | 1" | Globe control valve | AXS | 1DCA1A | Steam/Water | CL300 | RFFE | RFFE | 425 | 470 | S-40S | 1.0 " | Yes | 94.03.68.100.02.2 | HYDRO VALVE KIT | 2447 | PD-123B
02-TCV-AXS711 | CONDENSATE TANK SPARGING STEAM CONTROL VALVE | 02-3"-AXS1507-1DAA1A-1.5 "EOC | 3" | Globe control valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.100.02.1 | HYDRO VALVE KIT | 2448 | PD-050B
02-TCV-BFW716 | HP BYPASS SPRAY SUPPLY TCV | 02-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.100.01.0 |  | 2449 | PD-020B
02-TCV-BFW749 | CRH LETDOWN PCV SPRAY TCV | 02-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 2450 | PD-124B
02-TCV-BFW761 | CRH LETDOWN ATTEMPERATOR SPRAY TCV | 02-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 2451 | PD-124B
02-TCV-CCW181 | ACHE BYPASS CONTROL VALVE | 02-24"-CCW1141-1BAB2A | 24" | Butterfly control valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-20 |  | No | 94.03.68.100.02.3 |  | 2452 | PD-270B
02-TCV-CND706 | CRH VENTILATOR DSH SPRAY TCV | 02-2"-CND1062-1EAA2A-1.0 "MIC | 2" | Globe control valve | CND | 1EAA2A | Water | CL600 | RFFE | RFFE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.100.01.3 |  | 2453 | PD-030B
02-TCV-CND707 | HRH BYPASS SPRAY TCV | 02-4"-CND1256-1EAA2A-1.0 "MIC | 4" | Globe control valve | CND | 1EAA2A | Water | CL600 | RFFE | RFFE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.100.01.0 |  | 2454 | PD-034B
02-TCV-CND717 | HP DRAINS TANK QUENCH SPRAY TCV | 02-1.5"-CND1202-1EAA2A-1.0 "MOH | 1.5" | Globe control valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 2455 | PD-304B
02-TCV-CND718 | LP DRAINS TANK QUENCH SPRAY TCV | 02-2"-CND1200-1EAA2A-1.0 "MOH | 2" | Globe control valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 2456 | PD-305B
02-TCV-CND726 | LP BYPASS SPRAY TCV | 02-1"-CND1459-1EAA2A-1.0 "MIC | 1" | Globe control valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.100.01.0 |  | 2457 | PD-040B
02-TV-HPS123 | DRIP LEG DRAIN - AUTOMATED | 02-2"-HPS1015-1HBD2A-4.0 "EIC | 2" | Ball control valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 4.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 2458 | PD-021B
02-TV-HRH117 | DRIP LEG DRAIN | 02-2"-HRH1112-1FBD1A-4.0 "EIC | 2" | Ball control valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 2459 | PD-034B
02-TV-SWS717 | BLOWDOWN QUENCH CONTROL VALVE | 02-2"-SWS1016-1BAH1A-1.0 "MOH | 2" | Globe control valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 2460 | PD-090B
02-VAQA201 | UNIT 2 AFCU ISOLATION VALVE | 02-1"-AQA1001-1BCD2A | 1" | Ball valve | AQA | 1BCD2A | 19% Aqueous Ammonia | CL150 | RFFE | RFFE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 2461 | PD-782
02-VAXS101 | VENT | 02-0.75"-AXS1510-1DAA1A-1.5 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 2462 | PD-123B
02-VAXS102 | INSTRUMENT | 02-0.75"-AXS1072-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2463 | PD-050B
02-VAXS103 | TRAP ISOLATION | 02-0.75"-AXS1015-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2464 | PD-122B
02-VAXS104 | TRAP ISOLATION | 02-0.75"-AXS1004-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 2465 | PD-123B
02-VAXS105 | TRAP ISOLATION | 02-0.75"-AXS1004-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 2466 | PD-123B
02-VAXS106 | DRAIN | 02-0.75"-AXS1004-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 2467 | PD-123B
02-VAXS107 | TRAP BYPASS | 02-0.75"-AXS1151-1DAA1A-2.0 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 2468 | PD-123B
02-VAXS109 | INSTRUMENT | 02-2"-AXS1005-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 2469 | PD-123B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2470 | P&ID
02-VAXS110 | INSTRUMENT | 02-2"-AXS1019-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 2471 | PD-123B
02-VAXS113 | TRAP DRAIN | 02-2"-AXS1253-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2472 | PD-122B
02-VAXS117 | TRAP ISOLATION | 02-0.75"-AXS1132-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2473 | PD-123B
02-VAXS118 | TRAP ISOLATION | 02-0.75"-AXS1024-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2474 | PD-122B
02-VAXS119 | DRAIN | 02-0.75"-AXS1132-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2475 | PD-123B
02-VAXS120 | TRAP BYPASS | 02-0.75"-AXS1148-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 2476 | PD-123B
02-VAXS121 | VENT | 02-0.75"-AXS1503-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2477 | PD-123B
02-VAXS122 | INSTRUMENT | 02-0.75"-AXS1013-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2478 | PD-050B
02-VAXS123 | FG STARTUP FEEDWATER HX OUTLET CHECK VALVE | 02-2"-AXS1504-1DAA1A-1.0 "EOH | 2" | Check valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | SWING CHECK | 2479 | PD-123B
02-VAXS124 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE ISOLATION | 02-2"-AXS1504-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2480 | PD-123B
02-VAXS125 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE ISOLATION | 02-2"-AXS1505-1DCA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DCA1A | Steam/Water | CL800 | SWE | SWE | 425 | 470 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2481 | PD-123B
02-VAXS126 | DRAIN | 02-0.75"-AXS1504-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2482 | PD-123B
02-VAXS127 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE BYPASS | 02-0.75"-AXS1029-1DCA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DCA1A | Steam/Water | CL300 | SWE | SWE | 425 | 470 | S-40S | 1.0 " | Yes | 94.03.68.150.06.3H | THROTTLING SERVICE | 2483 | PD-123B
02-VAXS130 | DRIP LEG DRAIN | 02-2"-AXS1012-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2484 | PD-122B
02-VAXS132 | VENT | 02-0.75"-AXS1078-1DAA1A-1.5 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 2485 | PD-123B
02-VAXS133 | VENT | 02-0.75"-AXS1513-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2486 | PD-122B
02-VAXS135 | TRAP ISOLATION | 02-0.75"-AXS1237-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2487 | PD-122B
02-VAXS136 | TRAP ISOLATION | 02-0.75"-AXS1237-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2488 | PD-122B
02-VAXS137 | DRAIN | 02-0.75"-AXS1237-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2489 | PD-122B
02-VAXS138 | TRAP BYPASS | 02-0.75"-AXS1252-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 2490 | PD-122B
02-VAXS144 | DRAIN | 02-0.75"-AXS1001-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2491 | PD-122B
02-VAXS145 | ACC SPRAGING MODULATING CONTROL VALVE BYPASS | 02-2.5"-AXS1097-1DAA1A-1.0 "EOC | 2.5" | Globe valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.0 " | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 2492 | PD-050B
02-VAXS147 | DRAIN | 02-0.75"-AXS1509-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2493 | PD-050B
02-VAXS148 | SEAL STEAM REGULATION VALVE ISOLATION | 02-3"-AXS1511-1DAA1A-3.0 "EIC | 3" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 725 | S-40 | 3.0 " | No | 94.03.68.150.03.2H | FLEXIBLE WEDGE, EXTERNAL BYPASS VALVE | 2494 | PD-300B
02-VAXS149 | SEAL STEAM REGULATION VALVE ISOLATION | 02-4"-AXS1511-1DAA1A-3.0 "EIC | 4" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 725 | S-40 | 3.0 " | No | 94.03.68.150.03.2H | FLEXIBLE WEDGE, EXTERNAL BYPASS VALVE | 2495 | PD-300B
02-VAXS152 | DA EJECTOR SUPPLY CONTROL VALVE BYPASS | 02-1"-AXS1058-1DAA1A-1.0 "EOH | 1" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 2496 | PD-050B
02-VAXS153 | DRAIN | 02-0.75"-AXS1508-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2497 | PD-050B
02-VAXS156 | FG STARTUP FEEDWATER HX OUTLET CONTROL VALVE BYPASS | 02-2"-AXS1020-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 2498 | PD-123B
02-VAXS157 | INSTRUMENT | 02-0.75"-AXS1504-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Water | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2499 | PD-123B
02-VAXS158 | INSTRUMENT | 02-0.75"-AXS1503-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2500 | PD-123B
02-VAXS159 | SUPERHEATER/SEPARATOR ISOLATION | 02-3"-AXS1078-1DAA1A-1.5 "EIC | 3" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.150.03.0 | FLEXIBLE WEDGE, EXTERNAL BYPASS VALVE | 2501 | PD-123B
02-VAXS160 | DRAIN | 02-0.75"-AXS1015-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2502 | PD-122B
02-VAXS161 | TRAP ISOLATION | 02-0.75"-AXS1015-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2503 | PD-122B
02-VAXS164 | TRAP BYPASS | 02-0.75"-AXS1014-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 2504 | PD-122B
02-VAXS165 | ACC SPRAGING MODULATING CONTROL VALVE ISOLATION | 02-8"-AXS1047-1DAA1A-2.0 "EOH | 8" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 2.0 " | Yes | 94.03.68.150.03.0 | FLEXIBLE WEDGE, 3-WAY DRAIN | 2505 | PD-050B
02-VAXS166 | TRAP ISOLATION | 02-0.75"-AXS1024-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2506 | PD-122B
02-VAXS167 | TRAP BYPASS | 02-0.75"-AXS1025-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 2507 | PD-122B
02-VAXS168 | ACC SPARGING MODULATING CONTROL VALVE ISOLATION | 02-6"-AXS1507-1DAA1A-1.5 "EOC | 6" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.150.03.0 | FLEXIBLE WEDGE, 3-WAY DRAIN | 2508 | PD-050B
02-VAXS171 | FG STARTUP FEEDWATER HX/ SEPARATOR ISOLATION | 02-3"-AXS1070-1DAA1A-1.5 "EOC | 3" | Gate valve | AXS | 1DAA1A | Steam | CL300 | RFFE | RFFE | 425 | 470 | S-40 | 1.5 " | No | 94.03.68.150.03.0 | FLEXIBLE WEDGE, EXTERNAL BYPASS VALVE | 2509 | PD-123B
02-VAXS174 | DA EJECTOR CONTROL VALVE ISOLATION | 02-2"-AXS1508-1DAA1A-1.0 "EOC | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2510 | PD-050B
02-VAXS175 | DA EJECTOR CONTROL VALVE ISOLATION | 02-2"-AXS1048-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2511 | PD-050B
02-VAXS182 | VENT | 02-1"-AXS1075-1DAA1A-1.5 "EOC | 1" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 2512 | PD-050B
02-VAXS183 | VENT | 02-0.75"-AXS1048-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2513 | PD-050B
02-VAXS186 | INSTRUMENT | 02-0.75"-AXS1048-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2514 | PD-050B
02-VAXS187 | INSTRUMENT | 02-0.75"-AXS1500-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2515 | PD-123B
02-VAXS188 | INSTRUMENT | 02-0.75"-AXS1500-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 2516 | PD-123B
02-VAXS189 | TRAP ISOLATION | 02-0.75"-AXS1001-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2517 | PD-122B
02-VAXS190 | TRAP ISOLATION | 02-2"-AXS1071-1DAA1A-1.5 "EIC | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 2518 | PD-123B
02-VAXS191 | TRAP BYPASS | 02-0.75"-AXS1073-1DAA1A-1.5 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 2519 | PD-123B
02-VAXS194 | TRAP ISOLATION | 02-0.75"-AXS1073-1DAA1A-1.5 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 2520 | PD-123B
02-VAXS195 | DRAIN | 02-0.75"-AXS1073-1DAA1A-1.5 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 2521 | PD-123B
02-VAXS196 | SEAL STEAM CONTROL VALVE WARMING LINE ISOLATION | 02-0.75"-AXS1079-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 2522 | PD-123B
02-VAXS197 | SEAL STEAM CONTROL VALVE WARMING LINE THROTTLING | 02-0.75"-AXS1079-1DAA1A-2.0 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 2523 | PD-123B
02-VAXS198 | SEAL STEAM CONTROL VALVE WARMING LINE ISOLATION | 02-0.75"-AXS1079-1DAA1A-2.0 "EIC | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 2524 | PD-123B
02-VAXS199 | DRIP LEG DRAIN | 02-2"-AXS1027-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2525 | PD-122B
02-VAXS200 | DRIP LEG DRAIN | 02-2"-AXS1124-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2526 | PD-123B
02-VAXS201 | TRAP ISOLATION | 02-0.75"-AXS1132-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2527 | PD-123B
02-VAXS202 | TRAP BYPASS | 02-0.75"-AXS1076-1DAA1A-1.5 "EIC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.5 " | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 2528 | PD-123B
02-VAXS203 | DRAIN | 02-0.75"-AXS1024-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2529 | PD-122B
02-VAXS204 | SEAL STEAM REGULATING VALVE BYPASS | 02-2"-AXS1654-1DAA1A-2.5 "EIC | 2" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 725 | S-80 | 2.5 " | No | 94.03.68.150.06.2H | THROTTLING SERVICE | 2530 | PD-300B
02-VAXS289 | TRAP BYPASS | 02-0.75"-AXS1003-1DAA1A-1.0 "EOH | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | THROTTLING SERVICE | 2531 | PD-122B
02-VAXS290 | TRAP ISOLATION | 02-0.75"-AXS1001-1DAA1A-1.0 "EOH | 0.75" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2532 | PD-122B
02-VAXS291 | DRIP LEG DRAIN | 02-2"-AXS1008-1DAA1A-1.0 "EOH | 2" | Gate valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2533 | PD-122B
02-VAXS292 | VENT | 02-0.75"-AXS1500-1DAA1A-1.0 "EOC | 0.75" | Globe valve | AXS | 1DAA1A | Steam | CL800 | SWE | SWE | 425 | 470 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 2534 | PD-122B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2535 | P&ID
02-VBDN200 | INSTRUMENT ROOT VALVE | 02-0.5"-BDN1014-1BAA2A-1.0 "MOH | 0.5" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 2536 | PD-090B
02-VBDN201 | INSTRUMENT ROOT VALVE | 02-0.5"-BDN1014-1BAA2A-1.0 "MOH | 0.5" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 2537 | PD-090B
02-VBDN204 | VENT ROOT VALVE | 02-0.75"-BDN1024-1BAA2A-1.0 "MOH | 0.75" | Globe valve | BDN | 1BAA2A | Water | CL800 | SWE | SWE | 70 | 212 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2538 | PD-090B
02-VBDN219 | UNIT 2 BDN PUMP B DISCHARGE CHECK | 02-8"-BDN1682-1BAA2A-1.0 "MOH | 8" | Check valve | BDN | 1BAA2A | Water | CL150 | WAFER | WAFER | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | DUAL PLATE; MAX FLOW - 1600 GPM, MIN FLOW - 180 GPM | 2539 | PD-090B
02-VBDN220 | UNIT 2 BDN PUMP A DISCHARGE CHECK | 02-8"-BDN1024-1BAA2A-1.0 "MOH | 8" | Check valve | BDN | 1BAA2A | Water | CL150 | WAFER | WAFER | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | DUAL PLATE; MAX FLOW - 1600 GPM, MIN FLOW - 180 GPM | 2540 | PD-090B
02-VBDN223 | UNIT 2 BDN PUMP B DISCHARGE ISOLATION | 02-8"-BDN1682-1BAA2A-1.0 "MOH | 8" | Butterfly valve | BDN | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 2541 | PD-090B
02-VBDN224 | UNIT 2 BDN PUMP A DISCHARGE ISOLATION | 02-8"-BDN1024-1BAA2A-1.0 "MOH | 8" | Butterfly valve | BDN | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 70 | 212 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 |  | 2542 | PD-090B
02-VBFW101 | DRAIN VALVE | 02-1"-BFW1070-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2543 | PD-062B
02-VBFW103 | HRH TA SPRAY DRAIN | 02-0.75"-BFW1274-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2544 | PD-034B
02-VBFW105 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 02-6"-BFW1105-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2545 | PD-062B
02-VBFW106 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 02-6"-BFW1006-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2546 | PD-062B
02-VBFW107 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 02-6"-BFW1006-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2547 | PD-062B
02-VBFW108 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 02-6"-BFW1006-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2548 | PD-062B
02-VBFW109 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 02-6"-BFW1105-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2549 | PD-062B
02-VBFW110 | VENT VALVE | 02-0.75"-BFW1010-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2550 | PD-064B
02-VBFW111 | HRH TA SPRAY STRAINER ISOLATION | 02-6"-BFW1006-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2551 | PD-062B
02-VBFW112 | INSTRUMENT ISOLATION | 02-0.5"-BFW1025-1FAC1A-1.0 "EOH | 0.5" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2552 | PD-020B
02-VBFW113 | STRAINER DRAIN | 02-1"-BFW1077-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2553 | PD-062B
02-VBFW114 | INSTRUMENT ISOLATION | 02-0.5"-BFW1035-1FAC1A-1.0 "EOH | 0.5" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2554 | PD-020B
02-VBFW115 | STRAINER DRAIN | 02-1"-BFW1070-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2555 | PD-062B
02-VBFW116 | DRAIN VALVE | 02-1"-BFW1608-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2556 | PD-061B
02-VBFW117 | VENT VALVE | 02-0.75"-BFW1010-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2557 | PD-064B
02-VBFW118 | HRH TA SPRAY SUPPLY ISOLATION | 02-3"-BFW1108-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE | 2558 | PD-034B
02-VBFW119 | DRAIN VALVE | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2559 | PD-020B
02-VBFW120 | DRAIN VALVE | 02-0.75"-BFW1011-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2560 | PD-064B
02-VBFW121 | DRAIN VALVE | 02-0.75"-BFW1011-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2561 | PD-064B
02-VBFW123 | DRAIN VALVE | 02-1"-BFW1408-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2562 | PD-062B
02-VBFW128 | HPS BYPASS SPRAY ISOLATION | 02-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2563 | PD-062B
02-VBFW129 | HPS BYPASS SPRAY ISOLATION | 02-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2564 | PD-062B
02-VBFW130 | DRAIN VALVE | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2565 | PD-062B
02-VBFW131 | DRAIN VALVE | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2566 | PD-062B
02-VBFW132 | INSTRUMENT ISOLATION | 02-0.75"-BFW1019-1DAA1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1DAA1A | Water | CL800 | SWE | SWE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2567 | PD-060B
02-VBFW138 | DRAIN VALVE | 02-0.75"-BFW1018-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2568 | PD-061B
02-VBFW139 | DRAIN VALVE | 02-0.75"-BFW1018-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2569 | PD-061B
02-VBFW140 | INSTRUMENT ISOLATION | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2570 | PD-124B
02-VBFW141 | INSTRUMENT ISOLATION | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2571 | PD-124B
02-VBFW142 | INSTRUMENT ISOLATION | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2572 | PD-124B
02-VBFW143 | INSTRUMENT ISOLATION | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2573 | PD-124B
02-VBFW144 | DRAIN VALVE | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2574 | PD-124B
02-VBFW145 | DRAIN VALVE | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2575 | PD-124B
02-VBFW146 | CRH LETDOWN SPRAY SUPPLY ISOLATION | 02-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2576 | PD-124B
02-VBFW147 | VENT VALVE | 02-0.75"-BFW1018-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2577 | PD-061B
02-VBFW148 | CRH LETDOWN SPRAY SUPPLY CHECK | 02-1"-BFW1383-1FAC1A-1.0 "EOH | 1" | Check valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | PISTON CHECK | 2578 | PD-124B
02-VBFW149 | DRAIN VALVE | 02-1"-BFW1019-1DAA1A-1.0 "EOH | 1" | Gate valve | BFW | 1DAA1A | Water | CL800 | SWE | SWE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2579 | PD-060B
02-VBFW150 | VENT VALVE | 02-0.75"-BFW1018-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2580 | PD-061B
02-VBFW151 | VENT VALVE | 02-1"-BFW1069-1FAC1A-1.0 "EOH | 1" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2581 | PD-062B
02-VBFW152 | BFW SUCTION LP DRUM ISOLATION | 02-12"-BFW1019-1DAA1A-1.0 "EOH | 12" | Gate valve | BFW | 1DAA1A | Water | CL600 | BE | BE | 300 | 360 | S-STD | 1.0 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2582 | PD-060B
02-VBFW153 | VENT VALVE | 02-0.75"-BFW1461-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2583 | PD-064B
02-VBFW154 | INSTRUMENT ISOLATION | 02-0.75"-BFW1019-1DAA1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1DAA1A | Water | CL800 | SWE | SWE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2584 | PD-060B
02-VBFW155 | INSTRUMENT ISOLATION | 02-0.75"-BFW1019-1DAA1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1DAA1A | Water | CL800 | SWE | SWE | 300 | 360 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2585 | PD-060B
02-VBFW156 | INSTRUMENT ISOLATION | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2586 | PD-124B
02-VBFW157 | INSTRUMENT ISOLATION | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2587 | PD-124B
02-VBFW161 | VENT VALVE | 02-1"-BFW1069-1FAC1A-1.0 "EOH | 1" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2588 | PD-062B
02-VBFW162 | INSTRUMENT ISOLATION | 02-1"-BFW1076-1FAC1A-1.0 "EOH | 1" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2589 | PD-062B
02-VBFW163 | INSTRUMENT ISOLATION | 02-1"-BFW1076-1FAC1A-1.0 "EOH | 1" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2590 | PD-062B
02-VBFW164 | CRH AUX STEAM DSH SPRAY CHECK | 02-1"-BFW1156-1FAC1A-1.0 "EOH | 1" | Check valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | PISTON CHECK | 2591 | PD-124B
02-VBFW165 | DRAIN VALVE | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2592 | PD-063B
02-VBFW166 | DRAIN VALVE | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2593 | PD-063B
02-VBFW167 | BFP A IP DISCHARGE CHECK | 02-6"-BFW1374-1FAC1A-1.5 "EOH | 6" | Check valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 900 GPM, MIN FLOW- 140 GPM | 2594 | PD-060B
02-VBFW168 | DRAIN VALVE | 02-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2595 | PD-060B
02-VBFW169 | DRAIN VALVE | 02-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2596 | PD-060B
02-VBFW170 | INSTRUMENT ISOLATION | 02-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2597 | PD-060B
02-VBFW171 | INSTRUMENT ISOLATION | 02-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2598 | PD-060B
02-VBFW172 | VENT VALVE | 02-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2599 | PD-060B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2600 | P&ID
02-VBFW173 | VENT VALVE | 02-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2601 | PD-060B
02-VBFW174 | BFP B IP DISCHARGE CHECK | 02-6"-BFW1063-1FAC1A-1.5 "EOH | 6" | Check valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 900 GPM, MIN FLOW- 140 GPM | 2602 | PD-060B
02-VBFW175 | DRAIN VALVE | 02-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2603 | PD-060B
02-VBFW176 | DRAIN VALVE | 02-0.75"-BFW1063-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2604 | PD-060B
02-VBFW177 | INSTRUMENT ISOLATION | 02-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2605 | PD-060B
02-VBFW178 | INSTRUMENT ISOLATION | 02-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2606 | PD-060B
02-VBFW181 | INSTRUMENT ISOLATION | 02-0.75"-BFW1033-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2607 | PD-061B
02-VBFW182 | INSTRUMENT ISOLATION | 02-0.75"-BFW1033-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2608 | PD-061B
02-VBFW183 | INSTRUMENT ISOLATION | 02-0.75"-BFW1044-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2609 | PD-061B
02-VBFW184 | INSTRUMENT ISOLATION | 02-0.75"-BFW1044-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2610 | PD-061B
02-VBFW185 | INSTRUMENT ISOLATION | 02-0.75"-BFW1045-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2611 | PD-061B
02-VBFW186 | INSTRUMENT ISOLATION | 02-0.75"-BFW1045-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2612 | PD-061B
02-VBFW187 | INSTRUMENT ISOLATION | 02-0.75"-BFW1053-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2613 | PD-061B
02-VBFW188 | INSTRUMENT ISOLATION | 02-0.75"-BFW1053-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2614 | PD-061B
02-VBFW189 | VENT VALVE | 02-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2615 | PD-061B
02-VBFW190 | VENT VALVE | 02-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2616 | PD-061B
02-VBFW191 | BFP A HP DISCHARGE CHECK | 02-10"-BFW1029-1HAC2A-1.5 "EOH | 10" | Check valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 2500 GPM, MIN FLOW- 840 GPM | 2617 | PD-061B
02-VBFW192 | DRAIN VALVE | 02-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2618 | PD-061B
02-VBFW193 | DRAIN VALVE | 02-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2619 | PD-061B
02-VBFW194 | DRAIN VALVE | 02-1"-BFW1029-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2620 | PD-061B
02-VBFW195 | DRAIN VALVE | 02-1"-BFW1029-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2621 | PD-061B
02-VBFW196 | HP BFW FILL FROM CONDENSATE CHECK | 02-2"-BFW1608-1HAC2A-1.0 "EOH | 2" | Check valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | PISTON CHECK | 2622 | PD-061B
02-VBFW197 | HP BFW FILL FROM CONDENSATE STOP CHECK | 02-2"-BFW1608-1HAC2A-1.0 "EOH | 2" | Check Valve Locked Closed | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | GLOBE STOP CHECK | 2623 | PD-061B
02-VBFW198 | HP BFW FILL FROM CONDENSATE BLOCK | 02-2"-BFW1608-1HAC2A-1.0 "EOH | 2" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | FLOW UNDER PLUG | 2624 | PD-061B
02-VBFW199 | INSTRUMENT ISOLATION | 02-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2625 | PD-061B
02-VBFW200 | INSTRUMENT ISOLATION | 02-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2626 | PD-061B
02-VBFW209 | VENT VALVE | 02-0.75"-BFW1073-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2627 | PD-061B
02-VBFW210 | VENT VALVE | 02-0.75"-BFW1073-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2628 | PD-061B
02-VBFW211 | DRAIN VALVE | 02-0.75"-BFW1059-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2629 | PD-061B
02-VBFW212 | DRAIN VALVE | 02-0.75"-BFW1059-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2630 | PD-061B
02-VBFW213 | VENT VALVE | 02-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2631 | PD-061B
02-VBFW214 | VENT VALVE | 02-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2632 | PD-061B
02-VBFW215 | BFP A MIN RECIRC STRAINER ISOLATION | 02-6"-BFW1064-1HAC2A-1.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, EXTERNAL BONNET DRAIN | 2633 | PD-061B
02-VBFW216 | STRAINER DRAIN | 02-1.5"-BFW1031-1HAC2A-1.0 "EOH | 1.5" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2634 | PD-061B
02-VBFW217 | STRAINER DRAIN | 02-1.5"-BFW1031-1HAC2A-1.0 "EOH | 1.5" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2635 | PD-061B
02-VBFW218 | BFP A MIN RECIRC ACC ISOLATION | 02-6"-BFW1066-1HBB1A-1.5 "EOH | 6" | Ball valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 370 | 0.808" min | 1.5 " | Yes | 94.03.68.150.08.0 | FULL PORT, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED, 8" OPERATOR MOUNTING KIT | 2636 | PD-061B
02-VBFW219 | INSTRUMENT ISOLATION | 02-0.75"-BFW1060-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2637 | PD-061B
02-VBFW220 | INSTRUMENT ISOLATION | 02-0.75"-BFW1060-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2638 | PD-061B
02-VBFW221 | INSTRUMENT ISOLATION | 02-0.75"-BFW1061-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2639 | PD-061B
02-VBFW222 | INSTRUMENT ISOLATION | 02-0.75"-BFW1061-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2640 | PD-061B
02-VBFW223 | INSTRUMENT ISOLATION | 02-0.75"-BFW1062-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2641 | PD-061B
02-VBFW224 | INSTRUMENT ISOLATION | 02-0.75"-BFW1062-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2642 | PD-061B
02-VBFW225 | INSTRUMENT ISOLATION | 02-0.75"-BFW1068-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2643 | PD-061B
02-VBFW226 | INSTRUMENT ISOLATION | 02-0.75"-BFW1068-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2644 | PD-061B
02-VBFW227 | VENT VALVE | 02-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2645 | PD-061B
02-VBFW228 | VENT VALVE | 02-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2646 | PD-061B
02-VBFW229 | BFP B HP DISCHARGE CHECK | 02-10"-BFW1052-1HAC2A-1.5 "EOH | 10" | Check valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 2500 GPM, MIN FLOW- 840 GPM | 2647 | PD-061B
02-VBFW230 | VENT VALVE | 02-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2648 | PD-061B
02-VBFW231 | VENT VALVE | 02-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2649 | PD-061B
02-VBFW232 | BFP B MIN RECIRC STRAINER ISOLATION | 02-6"-BFW1072-1HAC2A-1.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, EXTERNAL BONNET DRAIN | 2650 | PD-061B
02-VBFW233 | STRAINER DRAIN | 02-1.5"-BFW1058-1HAC2A-1.0 "EOH | 1.5" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2651 | PD-061B
02-VBFW234 | STRAINER DRAIN | 02-1.5"-BFW1058-1HAC2A-1.0 "EOH | 1.5" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2652 | PD-061B
02-VBFW235 | DRAIN VALVE | 02-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2653 | PD-061B
02-VBFW236 | DRAIN VALVE | 02-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2654 | PD-061B
02-VBFW237 | DRAIN VALVE | 02-1"-BFW1052-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2655 | PD-061B
02-VBFW238 | DRAIN VALVE | 02-1"-BFW1052-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H | WEDGE GATE | 2656 | PD-061B
02-VBFW239 | BFP B MIN RECIRC ACC ISOLATION | 02-6"-BFW1074-1HBB1A-1.5 "EOH | 6" | Ball valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 370 | 0.808" min | 1.5 " | Yes | 94.03.68.150.08.0 | FULL PORT, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED, 8" OPERATOR MOUNTING KIT | 2657 | PD-061B
02-VBFW240 | DRAIN VALVE | 02-0.75"-BFW1149-1HBD1A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HBD1A | Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2658 | PD-020B
02-VBFW241 | DRAIN VALVE | 02-0.75"-BFW1149-1HBD1A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HBD1A | Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2659 | PD-020B
02-VBFW242 | INSTRUMENT ISOLATION | 02-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2660 | PD-020B
02-VBFW243 | INSTRUMENT ISOLATION | 02-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2661 | PD-020B
02-VBFW244 | INSTRUMENT ISOLATION | 02-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2662 | PD-020B
02-VBFW245 | INSTRUMENT ISOLATION | 02-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2663 | PD-020B
02-VBFW246 | VENT VALVE | 02-1"-BFW1000-1HAC2A-1.0 "EOH | 1" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2664 | PD-020B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2665 | P&ID
02-VBFW247 | VENT VALVE | 02-1"-BFW1000-1HAC2A-1.0 "EOH | 1" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2666 | PD-020B
02-VBFW248 | VENT VALVE | 02-1"-BFW1007-1HAC2A-1.0 "EOH | 1" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2667 | PD-020B
02-VBFW249 | VENT VALVE | 02-1"-BFW1007-1HAC2A-1.0 "EOH | 1" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2668 | PD-020B
02-VBFW250 | INSTRUMENT ISOLATION | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2669 | PD-062B
02-VBFW251 | INSTRUMENT ISOLATION | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2670 | PD-062B
02-VBFW252 | INSTRUMENT ISOLATION | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2671 | PD-062B
02-VBFW253 | INSTRUMENT ISOLATION | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2672 | PD-062B
02-VBFW254 | INSTRUMENT ISOLATION | 02-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2673 | PD-061B
02-VBFW255 | INSTRUMENT ISOLATION | 02-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2674 | PD-061B
02-VBFW256 | INSTRUMENT ISOLATION | 02-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2675 | PD-061B
02-VBFW257 | INSTRUMENT ISOLATION | 02-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2676 | PD-061B
02-VBFW258 | INSTRUMENT ISOLATION | 02-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2677 | PD-061B
02-VBFW259 | INSTRUMENT ISOLATION | 02-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2678 | PD-061B
02-VBFW260 | INSTRUMENT ISOLATION | 02-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2679 | PD-061B
02-VBFW261 | INSTRUMENT ISOLATION | 02-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2680 | PD-061B
02-VBFW262 | INSTRUMENT ISOLATION | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2681 | PD-064B
02-VBFW263 | BFP SUCTION FROM LPEC BYPASS CHECK | 02-8"-BFW1021-1EAA1A-1.0 "EOH | 8" | Check valve | BFW | 1EAA1A | Water | CL600 | BE | BE | 790 | 360 | S-40 | 1.0 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 2400 GPM, MIN FLOW- 840 GPM | 2682 | PD-060B
02-VBFW264 | BFP SUCTION ISOLATION FROM LPEC BYPASS | 02-8"-BFW1021-1EAA1A-1.0 "EOH | 8" | Gate valve | BFW | 1EAA1A | Water | CL600 | BE | BE | 790 | 360 | S-40 | 1.0 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2683 | PD-060B
02-VBFW265 | BFP A SUCTION ISOLATION | 02-12"-BFW1020-1DAA1A-1.0 "EOH | 12" | Gate valve | BFW | 1DAA1A | Water | CL600 | BE | BE | 300 | 360 | S-STD | 1.0 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2684 | PD-060B
02-VBFW266 | BFP B SUCTION ISOLATION | 02-12"-BFW1038-1DAA1A-1.0 "EOH | 12" | Gate valve | BFW | 1DAA1A | Water | CL600 | BE | BE | 300 | 360 | S-STD | 1.0 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2685 | PD-060B
02-VBFW267 | DRAIN VALVE | 02-0.75"-BFW1073-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2686 | PD-061B
02-VBFW269 | BFP A IP DISCHARGE ISOLATION | 02-6"-BFW1374-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2687 | PD-060B
02-VBFW270 | BFP B IP DISCHARGE ISOLATION | 02-6"-BFW1063-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2688 | PD-060B
02-VBFW271 | BFP A HP DISCHARGE ISOLATION | 02-10"-BFW1029-1HAC2A-1.5 "EOH | 10" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2689 | PD-061B
02-VBFW272 | BFP B HP DISCHARGE ISOLATION | 02-10"-BFW1052-1HAC2A-1.5 "EOH | 10" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | 1.082" min | 1.5 " | Yes | 94.03.68.150.01.0H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2690 | PD-061B
02-VBFW273 | INSTRUMENT ISOLATION | 02-0.75"-BFW1457-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2691 | PD-064B
02-VBFW274 | INSTRUMENT ISOLATION | 02-0.75"-BFW1459-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2692 | PD-064B
02-VBFW275 | INSTRUMENT ISOLATION | 02-0.75"-BFW1456-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2693 | PD-064B
02-VBFW276 | INSTRUMENT ISOLATION | 02-0.75"-BFW1460-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2694 | PD-064B
02-VBFW277 | VENT VALVE | 02-0.75"-BFW1434-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2695 | PD-064B
02-VBFW278 | INSTRUMENT ISOLATION | 02-0.75"-BFW1485-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2696 | PD-064B
02-VBFW279 | INSTRUMENT ISOLATION | 02-0.75"-BFW1453-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2697 | PD-064B
02-VBFW280 | INSTRUMENT ISOLATION | 02-0.75"-BFW1443-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2698 | PD-064B
02-VBFW281 | INSTRUMENT ISOLATION | 02-0.75"-BFW1479-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2699 | PD-064B
02-VBFW282 | INSTRUMENT ISOLATION | 02-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2700 | PD-064B
02-VBFW283 | VENT VALVE | 02-0.75"-BFW1041-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2701 | PD-064B
02-VBFW284 | INSTRUMENT ISOLATION | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2702 | PD-064B
02-VBFW285 | N2 CONNECTION | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2703 | PD-064B
02-VBFW286 | DRAIN VALVE | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2704 | PD-064B
02-VBFW287 | INSTRUMENT ISOLATION | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2705 | PD-064B
02-VBFW288 | INSTRUMENT ISOLATION | 02-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2706 | PD-064B
02-VBFW289 | DRAIN VALVE | 02-0.75"-BFW1434-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2707 | PD-064B
02-VBFW290 | FGH OUTLET RECIRC CV ISOLATION | 02-4"-BFW1442-1FAC1A-1.0 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2708 | PD-064B
02-VBFW291 | DRAIN VALVE | 02-0.75"-BFW1008-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2709 | PD-064B
02-VBFW292 | STRAINER DRAIN | 02-0.75"-BFW1094-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2710 | PD-064B
02-VBFW293 | INSTRUMENT ISOLATION | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2711 | PD-064B
02-VBFW294 | DRAIN VALVE | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2712 | PD-063B
02-VBFW295 | INSTRUMENT ISOLATION | 02-0.75"-BFW1079-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2713 | PD-063B
02-VBFW296 | INSTRUMENT ISOLATION | 02-0.75"-BFW1080-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2714 | PD-063B
02-VBFW297 | INSTRUMENT ISOLATION | 02-0.75"-BFW1080-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2715 | PD-063B
02-VBFW298 | INSTRUMENT ISOLATION | 02-0.75"-BFW1081-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2716 | PD-063B
02-VBFW299 | INSTRUMENT ISOLATION | 02-0.75"-BFW1081-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2717 | PD-063B
02-VBFW300 | CT TCA COOLER BFW INLET ISOLATION | 02-6"-BFW1028-1HAC2A-1.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2718 | PD-063B
02-VBFW301 | DRAIN VALVE | 02-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2719 | PD-063B
02-VBFW302 | DRAIN VALVE | 02-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2720 | PD-063B
02-VBFW303 | DRAIN VALVE | 02-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2721 | PD-063B
02-VBFW304 | DRAIN VALVE | 02-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2722 | PD-063B
02-VBFW305 | DRAIN VALVE | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2723 | PD-063B
02-VBFW306 | CT TCA COOLER BFW OUTLET ISOLATION | 02-6"-BFW1320-1HAC2A-2.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2724 | PD-063B
02-VBFW307 | INSTRUMENT ISOLATION | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2725 | PD-063B
02-VBFW308 | INSTRUMENT ISOLATION | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2726 | PD-063B
02-VBFW309 | INSTRUMENT ISOLATION | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2727 | PD-063B
02-VBFW310 | INSTRUMENT ISOLATION | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2728 | PD-063B
02-VBFW311 | INSTRUMENT ISOLATION | 02-0.75"-BFW1082-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2729 | PD-063B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2730 | P&ID
02-VBFW312 | INSTRUMENT ISOLATION | 02-0.75"-BFW1082-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2731 | PD-063B
02-VBFW313 | INSTRUMENT ISOLATION | 02-0.75"-BFW1083-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2732 | PD-063B
02-VBFW314 | INSTRUMENT ISOLATION | 02-0.75"-BFW1083-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2733 | PD-063B
02-VBFW315 | INSTRUMENT ISOLATION | 02-0.75"-BFW1084-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2734 | PD-063B
02-VBFW316 | INSTRUMENT ISOLATION | 02-0.75"-BFW1084-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2735 | PD-063B
02-VBFW317 | INSTRUMENT ISOLATION | 02-0.75"-BFW1085-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2736 | PD-063B
02-VBFW318 | INSTRUMENT ISOLATION | 02-0.75"-BFW1085-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2737 | PD-063B
02-VBFW319 | CRH LETDOWN SPRAY ISOLATION | 02-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2738 | PD-124B
02-VBFW320 | INSTRUMENT ISOLATION | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2739 | PD-063B
02-VBFW321 | INSTRUMENT ISOLATION | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2740 | PD-063B
02-VBFW322 | VENT VALVE | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2741 | PD-063B
02-VBFW323 | VENT VALVE | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2742 | PD-063B
02-VBFW324 | VENT VALVE | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2743 | PD-063B
02-VBFW325 | VENT VALVE | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2744 | PD-063B
02-VBFW326 | INSTRUMENT ISOLATION | 02-0.75"-BFW1324-1HBB1A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HBB1A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H |  | 2745 | PD-063B
02-VBFW327 | INSTRUMENT ISOLATION | 02-0.75"-BFW1324-1HBB1A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HBB1A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H |  | 2746 | PD-063B
02-VBFW328 | DRAIN VALVE | 02-0.75"-BFW1324-1HBB1A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HBB1A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2747 | PD-063B
02-VBFW329 | DRAIN VALVE | 02-0.75"-BFW1324-1HBB1A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HBB1A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2748 | PD-063B
02-VBFW330 | CT TCA COOLER BFW ISOLATION TO RECIRC | 02-6"-BFW1322-1HAC2A-2.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2749 | PD-063B
02-VBFW331 | VENT VALVE | 02-0.75"-BFW1040-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2750 | PD-063B
02-VBFW332 | VENT VALVE | 02-0.75"-BFW1040-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2751 | PD-063B
02-VBFW333 | DRAIN VALVE | 02-0.75"-BFW1087-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2752 | PD-063B
02-VBFW334 | DRAIN VALVE | 02-0.75"-BFW1087-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2753 | PD-063B
02-VBFW335 | DRAIN VALVE | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2754 | PD-063B
02-VBFW336 | DRAIN VALVE | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2755 | PD-063B
02-VBFW337 | DRAIN VALVE | 02-0.75"-BFW1073-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2756 | PD-061B
02-VBFW338 | DRAIN VALVE | 02-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2757 | PD-061B
02-VBFW339 | CT TCA COOLER RECIRC ACC ISOLATION | 02-6"-BFW1426-1HBB1A-2.5 "EOH | 6" | Ball valve | BFW | 1HBB1A | Water | CL2500 | BE | BE | 4100 | 705 | 0.808" min | 2.5 " | Yes | 94.03.68.150.08.0 | FULL PORT, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED, 8" OPERATOR MOUNTING KIT | 2758 | PD-063B
02-VBFW340 | INSTRUMENT ISOLATION | 02-0.75"-BFW1088-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2759 | PD-064B
02-VBFW341 | INSTRUMENT ISOLATION | 02-0.75"-BFW1088-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2760 | PD-064B
02-VBFW342 | INSTRUMENT ISOLATION | 02-0.75"-BFW1089-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2761 | PD-064B
02-VBFW343 | INSTRUMENT ISOLATION | 02-0.75"-BFW1089-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2762 | PD-064B
02-VBFW344 | FG HX AUTOMATIC BLOCK VALVE ISOLATION | 02-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2763 | PD-064B
02-VBFW345 | FG HX AUTOMATIC BLOCK VALVE ISOLATION | 02-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2764 | PD-064B
02-VBFW346 | FG HX WARMING VALVE ISOLATION | 02-1"-BFW1454-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2765 | PD-064B
02-VBFW347 | FG HX WARMING VALVE ISOLATION | 02-1"-BFW1454-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2766 | PD-064B
02-VBFW348 | N2 PURGE CONNECTION | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2767 | PD-064B
02-VBFW349 | VENT VALVE | 02-0.75"-BFW1041-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2768 | PD-064B
02-VBFW350 | FG HX BFW UPSTREAM ISOLATION | 02-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2769 | PD-064B
02-VBFW351 | DRAIN VALVE | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2770 | PD-064B
02-VBFW352 | FG HX BFW UPSTREAM ISOLATION | 02-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2771 | PD-064B
02-VBFW353 | FG HX LEAK DETECTION VENT | 02-0.75"-BFW1461-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2772 | PD-064B
02-VBFW354 | INSTRUMENT ISOLATION | 02-0.75"-BFW1456-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2773 | PD-064B
02-VBFW355 | INSTRUMENT ISOLATION | 02-0.75"-BFW1460-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2774 | PD-064B
02-VBFW356 | INSTRUMENT ISOLATION | 02-0.75"-BFW1457-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2775 | PD-064B
02-VBFW357 | INSTRUMENT ISOLATION | 02-0.75"-BFW1459-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2776 | PD-064B
02-VBFW359 | INSTRUMENT ISOLATION | 02-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2777 | PD-064B
02-VBFW360 | DRAIN VALVE | 02-0.75"-BFW1434-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2778 | PD-064B
02-VBFW361 | FG HX RECIRC ISOLATION | 02-4"-BFW1442-1FAC1A-1.0 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2779 | PD-064B
02-VBFW362 | DRAIN VALVE | 02-0.75"-BFW1009-1FBD1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FBD1A | Water | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2780 | PD-034B
02-VBFW363 | DRAIN VALVE | 02-0.75"-BFW1009-1FBD1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FBD1A | Water | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2781 | PD-034B
02-VBFW364 | DRAIN VALVE | 02-0.75"-BFW1008-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2782 | PD-064B
02-VBFW365 | DRAIN VALVE | 02-0.75"-BFW1072-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.2H | WEDGE GATE | 2783 | PD-061B
02-VBFW366 | DRAIN VALVE | 02-0.75"-BFW1094-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2784 | PD-064B
02-VBFW367 | FG HX OUTLET ISOLATION TO CND | 02-4"-BFW1008-1FAC1A-1.0 "EOH | 4" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2785 | PD-064B
02-VBFW368 | FG HX OUTLET TO CND CHECK | 02-4"-BFW1067-1EAA1A-1.0 "EOH | 4" | Check valve | BFW | 1EAA1A | Water | CL600 | BE | BE | 790 | 589 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; MAX FLOW 230 GPM, MIN FLOW 15 GPM | 2786 | PD-064B
02-VBFW369 | FG HX LEAK DETECTION VENT | 02-0.75"-BFW1434-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2787 | PD-064B
02-VBFW370 | INSTRUMENT ISOLATION | 02-0.75"-BFW1443-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2788 | PD-064B
02-VBFW371 | INSTRUMENT ISOLATION | 02-0.75"-BFW1479-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2789 | PD-064B
02-VBFW372 | INSTRUMENT ISOLATION | 02-0.75"-BFW1485-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2790 | PD-064B
02-VBFW373 | INSTRUMENT ISOLATION | 02-0.75"-BFW1453-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2791 | PD-064B
02-VBFW374 | HPS TA SPRAY SUPPLY CHECK | 02-3"-BFW1149-1HBD1A-2.0 "EOH | 3" | Check valve | BFW | 1HBD1A | Water | CL2500 SPL | BE | BE | 2534 | 1097 | S-XXS | 2.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; MAX FLOW 215 GPM, MIN FLOW 50 GPM | 2792 | PD-020B
02-VBFW375 | HPS TA SPRAY STRAINER ISOLATION | 02-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2793 | PD-020B
02-VBFW376 | HPS TA SPRAY STRAINER ISOLATION | 02-3"-BFW1153-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2794 | PD-020B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2795 | P&ID
02-VBFW377 | DRAIN VALVE | 02-1"-BFW1012-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2796 | PD-020B
02-VBFW378 | INSTRUMENT ISOLATION | 02-0.5"-BFW1025-1FAC1A-1.0 "EOH | 0.5" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2797 | PD-020B
02-VBFW379 | FG HX OUTLET RECIRC CV OUTLET ISOLATION | 02-4"-BFW1093-1FBB1A-1.0 "EOH | 4" | Ball valve | BFW | 1FBB1A | Water | CL1500 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.08.0 | FULL PORT, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED | 2798 | PD-064B
02-VBFW380 | STRAINER DRAIN | 02-1"-BFW1001-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2799 | PD-020B
02-VBFW381 | DRAIN VALVE | 02-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2800 | PD-061B
02-VBFW382 | DRAIN VALVE | 02-0.75"-BFW1067-1EAA1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1EAA1A | Water | CL800 | SWE | SWE | 790 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2801 | PD-053B
02-VBFW383 | HPS TA SPRAY STRAINER ISOLATION | 02-3"-BFW1153-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2802 | PD-020B
02-VBFW384 | INSTRUMENT ISOLATION | 02-0.75"-BFW1079-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2803 | PD-063B
02-VBFW386 | INSTRUMENT ISOLATION | 02-0.75"-BFW1078-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2804 | PD-063B
02-VBFW387 | DRAIN VALVE | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2805 | PD-020B
02-VBFW388 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 02-6"-BFW1105-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2806 | PD-062B
02-VBFW389 | HRH TA SPRAY SUPPLY DRAIN | 02-0.75"-BFW1274-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2807 | PD-034B
02-VBFW390 | STRAINER DRAIN | 02-1"-BFW1077-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2808 | PD-062B
02-VBFW391 | SHARED SPRAY SUPPLY STRAINER ISOLATION | 02-6"-BFW1105-1FAC1A-1.5 "EOH | 6" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2809 | PD-062B
02-VBFW392 | HRH TA SPRAY SUPPLY CHECK | 02-3"-BFW1009-1FBD1A-1.5 "EOH | 3" | Check valve | BFW | 1FBD1A | Water | CL900 | BE | BE | 586 | 1096 | S-40 | 1.5 " | Yes | 94.03.68.150.01.1H | TILTING DISC; MAX FLOW 250 GPM, MIN FLOW 50 GPM | 2810 | PD-034B
02-VBFW402 | DRAIN VALVE | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2811 | PD-064B
02-VBFW403 | DRAIN VALVE | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2812 | PD-064B
02-VBFW404 | INSTRUMENT ISOLATION | 02-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2813 | PD-060B
02-VBFW405 | INSTRUMENT ISOLATION | 02-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2814 | PD-060B
02-VBFW406 | INSTRUMENT ISOLATION | 02-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2815 | PD-060B
02-VBFW407 | INSTRUMENT ISOLATION | 02-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2816 | PD-060B
02-VBFW408 | IP BFW FILL FROM CONDENSATE CHECK | 02-2"-BFW1408-1FAC1A-1.0 "EOH | 2" | Check valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | PISTON CHECK | 2817 | PD-062B
02-VBFW409 | IP BFW FILL FROM CONDENSATE STOP CHECK | 02-2"-BFW1408-1FAC1A-1.0 "EOH | 2" | Check Valve Locked Closed | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | GLOBE STOP CHECK | 2818 | PD-062B
02-VBFW410 | IP BFW FILL FROM CONDENSATE BLOCK | 02-2"-BFW1408-1FAC1A-1.0 "EOH | 2" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H | FLOW UNDER PLUG | 2819 | PD-062B
02-VBFW411 | STRAINER VENT | 02-1.5"-BFW1030-1HAC2A-1.0 "EOH | 1.5" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2820 | PD-061B
02-VBFW412 | STRAINER VENT | 02-1.5"-BFW1030-1HAC2A-1.0 "EOH | 1.5" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2821 | PD-061B
02-VBFW415 | DRAIN VALVE | 02-0.75"-BFW1064-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2822 | PD-061B
02-VBFW416 | VENT VALVE | 02-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2823 | PD-062B
02-VBFW417 | VENT VALVE | 02-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2824 | PD-062B
02-VBFW422 | DRAIN VALVE | 02-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2825 | PD-061B
02-VBFW423 | DRAIN VALVE | 02-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2826 | PD-061B
02-VBFW424 | INSTRUMENT ISOLATION | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2827 | PD-062B
02-VBFW425 | VENT VALVE | 02-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2828 | PD-061B
02-VBFW426 | VENT VALVE | 02-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2829 | PD-061B
02-VBFW427 | STRAINER VENT | 02-1.5"-BFW1054-1HAC2A-1.0 "EOH | 1.5" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2830 | PD-061B
02-VBFW428 | STRAINER VENT | 02-1.5"-BFW1054-1HAC2A-1.0 "EOH | 1.5" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2831 | PD-061B
02-VBFW429 | BFW SUCTION LP DRUM SUPPLY CHECK | 02-12"-BFW1019-1DAA1A-1.0 "EOH | 12" | Check valve | BFW | 1DAA1A | Water | CL600 | BE | BE | 300 | 360 | S-STD | 1.0 " | Yes | 94.03.68.150.01.0H | TILTING DISC; MAX FLOW- 2910 GPM, MIN FLOW- 840 GPM | 2832 | PD-060B
02-VBFW430 | VENT VALVE | 02-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2833 | PD-060B
02-VBFW431 | INSTRUMENT ISOLATION | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2834 | PD-124B
02-VBFW432 | INSTRUMENT ISOLATION | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2835 | PD-124B
02-VBFW433 | IP BFW TO CRH LETDOWN SPRAY ISOLATION | 02-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2836 | PD-124B
02-VBFW434 | IP BFW TO CRH LETDOWN SPRAY ISOLATION | 02-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2837 | PD-124B
02-VBFW435 | INSTRUMENT ISOLATION | 02-0.75"-BFW1078-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2838 | PD-063B
02-VBFW436 | DRAIN VALVE | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2839 | PD-124B
02-VBFW437 | DRAIN VALVE | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2840 | PD-124B
02-VBFW438 | INSTRUMENT ISOLATION | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2841 | PD-062B
02-VBFW439 | INSTRUMENT ISOLATION | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2842 | PD-064B
02-VBFW440 | STRAINER VENT | 02-0.75"-BFW1037-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2843 | PD-064B
02-VBFW441 | STRAINER VENT | 02-0.75"-BFW1037-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2844 | PD-064B
02-VBFW442 | INSTRUMENT ISOLATION | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2845 | PD-064B
02-VBFW443 | INSTRUMENT ISOLATION | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2846 | PD-064B
02-VBFW444 | INSTRUMENT ISOLATION | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2847 | PD-064B
02-VBFW445 | INSTRUMENT ISOLATION | 02-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2848 | PD-064B
02-VBFW447 | DRAIN VALVE | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2849 | PD-124B
02-VBFW448 | DRAIN VALVE | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2850 | PD-124B
02-VBFW449 | DRAIN VALVE | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2851 | PD-064B
02-VBFW450 | DRAIN VALVE | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2852 | PD-064B
02-VBFW451 | DRAIN VALVE | 02-0.75"-BFW1156-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2853 | PD-124B
02-VBFW452 | DRAIN VALVE | 02-0.75"-BFW1156-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2854 | PD-124B
02-VBFW453 | DRAIN VALVE | 02-0.75"-BFW1383-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2855 | PD-124B
02-VBFW454 | DRAIN VALVE | 02-0.75"-BFW1383-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2856 | PD-124B
02-VBFW459 | VENT VALVE | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2857 | PD-064B
02-VBFW460 | VENT VALVE | 02-0.75"-BFW1442-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2858 | PD-064B
02-VBFW461 | DRAIN VALVE | 02-0.75"-BFW1473-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2859 | PD-064B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2860 | P&ID
02-VBFW462 | DRAIN VALVE | 02-0.75"-BFW1473-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2861 | PD-064B
02-VBFW503 | STRAINER DRAIN | 02-1"-BFW1012-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2862 | PD-020B
02-VBFW505 | HPS TA SPRAY SUPPLY ISOLATION | 02-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2863 | PD-020B
02-VBFW506 | VENT VALVE | 02-0.75"-BFW1374-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0H |  | 2864 | PD-060B
02-VBFW509 | STRAINER DRAIN | 02-1"-BFW1001-1HAC2A-1.0 "EOH | 1" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2865 | PD-020B
02-VBFW513 | HPS BYPASS SPRAY SUPPLY ISOLATION | 02-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2866 | PD-020B
02-VBFW519 | INSTRUMENT ISOLATION | 02-0.5"-BFW1035-1FAC1A-1.0 "EOH | 0.5" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2867 | PD-020B
02-VBFW521 | HPS TA SPRAY STRAINER ISOLATION | 02-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS |  | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2868 | PD-020B
02-VBFW523 | HPS TA SPRAY STRAINER ISOLATION | 02-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2869 | PD-020B
02-VBFW525 | HPS TA SPRAY STRAINER ISOLATION | 02-3"-BFW1153-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2870 | PD-020B
02-VBFW529 | DRAIN VALVE | 02-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2871 | PD-020B
02-VBFW531 | HPS TA SPRAY SUPPLY ISOLATION | 02-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS |  | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2872 | PD-020B
02-VBFW532 | STRAINER VENT | 02-0.75"-BFW1086-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2873 | PD-063B
02-VBFW539 | HPS BYPASS SPRAY SUPPLY CHECK | 02-3"-BFW1145-1FBB1A-1.5 "EOH | 3" | Check valve | BFW | 1FBB1A | Water | CL900 | BE | BE | 1400 | 500 | S-80 | 1.5 " | Yes | 94.03.68.150.01.1H | TILTING DISC; MAX FLOW 350 GPM, MIN FLOW 80 GPM | 2874 | PD-020B
02-VBFW545 | DRAIN VALVE | 02-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2875 | PD-020B
02-VBFW547 | DRAIN VALVE | 02-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2876 | PD-020B
02-VBFW549 | HPS TA SPRAY STRAINER ISOLATION | 02-3"-BFW1153-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2877 | PD-020B
02-VBFW551 | DRAIN VALVE | 02-0.75"-BFW1145-1FBB1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FBB1A | Water | CL1500 | SWE | SWE | 1400 | 500 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2878 | PD-020B
02-VBFW553 | DRAIN VALVE | 02-0.75"-BFW1150-1HAC2A-1.0 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2879 | PD-020B
02-VBFW555 | HPS TA SPRAY STRAINER ISOLATION | 02-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS |  | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2880 | PD-020B
02-VBFW557 | DRAIN VALVE | 02-0.75"-BFW1145-1FBB1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FBB1A | Water | CL1500 | SWE | SWE | 1400 | 500 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2881 | PD-020B
02-VBFW567 | VENT VALVE | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2882 | PD-020B
02-VBFW569 | VENT VALVE | 02-0.75"-BFW1006-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2883 | PD-020B
02-VBFW570 | ISOLATION TO CRH LETDOWN ATTEMPERATORS | 02-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2884 | PD-124B
02-VBFW571 | ISOLATION TO CRH LETDOWN ATTEMPERATORS | 02-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2885 | PD-124B
02-VBFW572 | DRAIN VALVE | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2886 | PD-124B
02-VBFW573 | DRAIN VALVE | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2887 | PD-124B
02-VBFW574 | ISOLATION TO HRH TA SPRAY | 02-3"-BFW1108-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | PARALLEL SLIDE, 3-WAY DRAIN | 2888 | PD-062B
02-VBFW575 | ISOLATION TO HRH TA SPRAY | 02-3"-BFW1108-1FAC1A-1.0 "EOH | 3" | Gate valve | BFW | 1FAC1A | Water | CL900 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN | 2889 | PD-062B
02-VBFW576 | DRAIN VALVE | 02-0.75"-BFW1108-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2890 | PD-062B
02-VBFW577 | DRAIN VALVE | 02-0.75"-BFW1108-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 2891 | PD-062B
02-VBFW578 | VENT VALVE | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2892 | PD-064B
02-VBFW579 | VENT VALVE | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2893 | PD-064B
02-VBFW600 | VENT VALVE | 02-0.75"-BFW1002-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2894 | PD-064B
02-VBFW601 | VENT VALVE | 02-0.75"-BFW1002-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2895 | PD-064B
02-VBFW602 | DRAIN VALVE | 02-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2896 | PD-064B
02-VBFW603 | DRAIN VALVE | 02-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2897 | PD-064B
02-VBFW604 | VENT VALVE | 02-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2898 | PD-061B
02-VBFW605 | VENT VALVE | 02-0.75"-BFW1029-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2899 | PD-061B
02-VBFW606 | VENT VALVE | 02-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2900 | PD-061B
02-VBFW607 | VENT VALVE | 02-0.75"-BFW1052-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2901 | PD-061B
02-VBFW608 | VENT VALVE | 02-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2902 | PD-061B
02-VBFW609 | VENT VALVE | 02-0.75"-BFW1039-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2903 | PD-061B
02-VBFW610 | DRAIN VALVE | 02-0.75"-BFW1040-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2904 | PD-063B
02-VBFW611 | DRAIN VALVE | 02-0.75"-BFW1040-1HAC2A-1.5 "EOH | 0.75" | Gate valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2905 | PD-063B
02-VBFW612 | VENT VALVE | 02-0.75"-BFW1149-1HBD1A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HBD1A | Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H |  | 2906 | PD-020B
02-VBFW613 | VENT VALVE | 02-0.75"-BFW1149-1HBD1A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HBD1A | Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 1.5 " | Yes | 94.03.68.150.02.3H |  | 2907 | PD-020B
02-VBFW614 | VENT VALVE | 02-0.75"-BFW1321-1HAC2A-2.0 "EIC | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 2.0 " | No | 94.03.68.150.02.3H |  | 2908 | PD-063B
02-VBFW615 | VENT VALVE | 02-0.75"-BFW1321-1HAC2A-2.0 "EIC | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 2.0 " | No | 94.03.68.150.02.3H |  | 2909 | PD-063B
02-VBFW616 | DRAIN VALVE | 02-0.75"-BFW1057-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2910 | PD-064B
02-VBFW617 | DRAIN VALVE | 02-0.75"-BFW1057-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2911 | PD-064B
02-VBFW618 | VENT VALVE | 02-0.75"-BFW1009-1FBD1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FBD1A | Water | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2912 | PD-034B
02-VBFW619 | VENT VALVE | 02-0.75"-BFW1009-1FBD1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FBD1A | Water | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2913 | PD-034B
02-VBFW622 | VENT VALVE | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2914 | PD-124B
02-VBFW623 | VENT VALVE | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2915 | PD-124B
02-VBFW624 | VENT VALVE | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2916 | PD-124B
02-VBFW625 | VENT VALVE | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 2917 | PD-124B
02-VBFW626 | DRAIN VALVE | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2918 | PD-124B
02-VBFW627 | DRAIN VALVE | 02-0.75"-BFW1699-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2919 | PD-124B
02-VBFW628 | DRAIN VALVE | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2920 | PD-124B
02-VBFW629 | DRAIN VALVE | 02-0.75"-BFW1036-1FAC1A-1.0 "EOH | 0.75" | Gate valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 2921 | PD-124B
02-VBFW630 | INSTRUMENT ISOLATION | 02-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2 |  | 2922 | PD-064B
02-VBFW631 | INSTRUMENT ISOLATION | 02-0.75"-BFW1471-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2 |  | 2923 | PD-064B
02-VBFW700 | INSTRUMENT ISOLATION | 02-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2924 | PD-063B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2925 | P&ID
02-VBFW701 | INSTRUMENT ISOLATION | 02-0.75"-BFW1028-1HAC2A-1.0 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2926 | PD-063B
02-VBFW922 | CTA COOLER BFW OUTLET RECIRC CV ISOLATION | 02-6"-BFW1322-1HAC2A-2.5 "EOH | 6" | Gate valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 705 | S-XXS | 2.5 " | Yes | 94.03.68.150.01.1H | DOUBLE DISC WEDGE, EXTERNAL BONNET DRAIN | 2927 | PD-063B
02-VBFW923 | STRAINER VENT | 02-0.75"-BFW1086-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2928 | PD-063B
02-VBFW924 | INSTRUMENT ISOLATION | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2929 | PD-063B
02-VBFW925 | INSTRUMENT ISOLATION | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2930 | PD-063B
02-VBFW926 | INSTRUMENT ISOLATION | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2931 | PD-063B
02-VBFW927 | INSTRUMENT ISOLATION | 02-0.75"-BFW1322-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2932 | PD-063B
02-VBFW928 | INSTRUMENT ISOLATION | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2933 | PD-063B
02-VBFW929 | INSTRUMENT ISOLATION | 02-0.75"-BFW1320-1HAC2A-1.5 "EOH | 0.75" | Globe valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 705 | S-160 | 1.5 " | Yes | 94.03.68.150.02.1H |  | 2934 | PD-063B
02-VBFW933 | INSTRUMENT ISOLATION | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2935 | PD-064B
02-VBFW934 | INSTRUMENT ISOLATION | 02-0.75"-BFW1438-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2936 | PD-064B
02-VBFW935 | INSTRUMENT ISOLATION | 02-0.75"-BFW1473-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2937 | PD-064B
02-VBFW936 | INSTRUMENT ISOLATION | 02-0.75"-BFW1473-1FAC1A-1.0 "EOH | 0.75" | Globe valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 2938 | PD-064B
02-VCCF104 | UNIT 2 ENCLOSURE CONTAINMENT DRAIN ISOLATION VALVE | 02-2"-CCF1004-1BAA2A-1.0 "MOH | 2" | Ball valve | CCF | 1BAA2A | 19% Aqueous Ammonia and | CL600 | SWE | SWE | 0 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2939 | PD-520B
02-VCCF105 | UNIT 2 CONDENSATE AMMONIA FEED ISOLATION VALVE | 02-0.375"-CCF1030-1LCR1A-1.0 "MOH | 0.375" | Ball valve | CCF | 1LCR1A | 19% Aqueous Ammonia | CL900 | CTE | CTE | 790 | 115 | 0.065" Avg. Wall | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2940 | PD-053B
02-VCCW100 | INSTRUMENTATION | 02-0.75"-CCW1128-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 2941 | PD-271B
02-VCCW101 | INSTRUMENTATION | 02-0.75"-CCW1105-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 2942 | PD-271B
02-VCCW102 | HEAD TANK TO PUMP SUCTION ISOLATION | 02-2"-CCW1029-1BCA3A-1.0 "MOH | 2" | Ball valve | CCW | 1BCA3A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2943 | PD-270B
02-VCCW103 | CCW HEAD TANK DRAIN | 02-2"-CCW1051-1BCA3A-1.0 "MOH | 2" | Gate valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2944 | PD-270B
02-VCCW104 | INSTRUMENTATION | 02-0.75"-CCW1006-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2945 | PD-270B
02-VCCW105 | ACHE OUTLET ISOLATION/THROTTLING | 02-12"-CCW1105-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 2946 | PD-271B
02-VCCW106 | PUMP SUCTION ISOLATION | 02-24"-CCW1006-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 2947 | PD-270B
02-VCCW107 | PUMP DISCHARGE ISOLATION | 02-24"-CCW1023-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 2948 | PD-270B
02-VCCW108 | ACHE OUTLET ISOLATION/THROTTLING | 02-12"-CCW1108-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 2949 | PD-271B
02-VCCW109 | PUMP DISCHARGE ISOLATION | 02-24"-CCW1008-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 2950 | PD-270B
02-VCCW110 | VENT | 02-0.75"-CCW1111-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2951 | PD-271B
02-VCCW111 | VENT | 02-0.75"-CCW1045-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2952 | PD-270B
02-VCCW112 | VENT | 02-0.75"-CCW1046-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2953 | PD-270B
02-VCCW113 | DRAIN | 02-0.75"-CCW1023-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2954 | PD-270B
02-VCCW114 | POT FEEDER INLET ISOLATION | 02-2"-CCW1043-1BAB2A | 2" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2955 | PD-270B
02-VCCW115 | INSTRUMENTATION | 02-0.75"-CCW1006-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2956 | PD-270B
02-VCCW116 | INSTRUMENTATION | 02-0.75"-CCW1205-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 2957 | PD-272B
02-VCCW117 | DRAIN | 02-0.75"-CCW1049-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2958 | PD-270B
02-VCCW118 | PUMP DISCHARGE CHECK | 02-24"-CCW1008-1BAB2A | 24" | Check valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | WAFER | WAFER | 150 | 150 | S-20 |  | No | 94.03.68.150.03.0 | DUAL PLATE, MAX FLOW - 12200 GPM, MIN FLOW - 7000 GPM | 2959 | PD-270B
02-VCCW119 | INSTRUMENTATION | 02-0.75"-CCW1006-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2960 | PD-270B
02-VCCW120 | ACHE INLET ISOLATION | 02-12"-CCW1120-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 2961 | PD-271B
02-VCCW121 | PUMP SUCTION ISOLATION | 02-24"-CCW1015-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 2962 | PD-270B
02-VCCW122 | INSTRUMENTATION | 02-0.75"-CCW1015-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2963 | PD-270B
02-VCCW123 | ACHE INLET ISOLATION | 02-12"-CCW1123-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 2964 | PD-271B
02-VCCW124 | VENT | 02-0.75"-CCW1113-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2965 | PD-271B
02-VCCW125 | ACHE OUTLET ISOLATION/THROTTLING | 02-12"-CCW1128-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 2966 | PD-271B
02-VCCW126 | BYPASS FOR ACHE BYPASS CV | 02-24"-CCW1127-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.2 | THROTTLING SERVICE | 2967 | PD-270B
02-VCCW127 | PUMP DISCHARGE CHECK | 02-24"-CCW1023-1BAB2A | 24" | Check valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | WAFER | WAFER | 150 | 150 | S-20 |  | No | 94.03.68.150.03.0 | DUAL PLATE, MAX FLOW - 12200 GPM, MIN FLOW - 7000 GPM | 2968 | PD-270B
02-VCCW128 | INSTRUMENTATION | 02-0.75"-CCW1001-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 2969 | PD-275B
02-VCCW129 | ACHE INLET HEADER ISOLATION | 02-24"-CCW1129-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 2970 | PD-271B
02-VCCW130 | INSTRUMENTATION | 02-2"-CCW1030-1BCA3A-1.0 "MOH | 2" | Globe valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 2971 | PD-270B
02-VCCW131 | INSTRUMENTATION | 02-0.75"-CCW1023-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2972 | PD-270B
02-VCCW132 | DRAIN | 02-2"-CCW1026-1BAB2A | 2" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2973 | PD-270B
02-VCCW133 | POT FEEDER OUTLET ISOLATION/THROTTLING | 02-2"-CCW1044-1BAB2A | 2" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 | THROTTLING SERVICE | 2974 | PD-270B
02-VCCW134 | DRAIN | 02-0.75"-CCW1008-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2975 | PD-270B
02-VCCW135 | INSTRUMENTATION | 02-0.75"-CCW1008-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2976 | PD-270B
02-VCCW136 | VENT | 02-0.75"-CCW1008-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2977 | PD-270B
02-VCCW137 | INSTRUMENTATION | 02-0.75"-CCW1015-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2978 | PD-270B
02-VCCW138 | INSTRUMENTATION | 02-0.75"-CCW1015-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2979 | PD-270B
02-VCCW139 | DRAIN | 02-0.75"-CCW1027-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2980 | PD-270B
02-VCCW140 | DRAIN | 02-0.75"-CCW1141-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2981 | PD-270B
02-VCCW141 | DRAIN | 02-0.75"-CCW1050-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2982 | PD-270B
02-VCCW142 | POT FEEDER OUTLET ISOLATION/THROTTLING | 02-0.75"-CCW1044-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 2983 | PD-270B
02-VCCW143 | VENT | 02-0.75"-CCW1115-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2984 | PD-271B
02-VCCW144 | ACHE INLET ISOLATION | 02-12"-CCW1142-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 2985 | PD-271B
02-VCCW145 | ACHE INLET ISOLATION | 02-12"-CCW1145-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 2986 | PD-271B
02-VCCW146 | VENT | 02-0.75"-CCW1114-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2987 | PD-271B
02-VCCW147 | VENT | 02-0.75"-CCW1012-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 2988 | PD-275B
02-VCCW148 | ACHE BYPASS CV ISOLATION | 02-24"-CCW1141-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 2989 | PD-270B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 2990 | P&ID
02-VCCW149 | ACHE BYPASS CV ISOLATION | 02-24"-CCW1141-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 150 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 2991 | PD-270B
02-VCCW150 | VENT | 02-0.75"-CCW1112-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2992 | PD-271B
02-VCCW151 | DRAIN | 02-0.75"-CCW1042-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2993 | PD-270B
02-VCCW152 | DRAIN | 02-2"-CCW1022-1BAB2A | 2" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2994 | PD-270B
02-VCCW153 | SYSTEM BALANCING CV ISOLATION | 02-16"-CCW1141-1BAB2A | 16" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 2995 | PD-270B
02-VCCW154 | SYSTEM BALANCING CV ISOLATION | 02-16"-CCW1141-1BAB2A | 16" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 2996 | PD-270B
02-VCCW155 | SYSTEM BALANCING CV BYPASS | 02-10"-CCW1013-1BAB2A | 10" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.2H | THROTTLING SERVICE | 2997 | PD-270B
02-VCCW156 | DRAIN | 02-0.75"-CCW1141-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 2998 | PD-270B
02-VCCW157 | INSTRUMENTATION | 02-0.75"-CCW1167-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 2999 | PD-271B
02-VCCW158 | VENT | 02-0.75"-CCW1009-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 3000 | PD-270B
02-VCCW159 | VENT | 02-0.75"-CCW1019-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 3001 | PD-270B
02-VCCW160 | ACHE INLET ISOLATION | 02-12"-CCW1160-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-STD |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 3002 | PD-271B
02-VCCW161 | VENT | 02-0.75"-CCW1031-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3003 | PD-275B
02-VCCW162 | INSTRUMENTATION | 02-0.75"-CCW1031-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3004 | PD-275B
02-VCCW163 | INSTRUMENTATION | 02-0.75"-CCW1014-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3005 | PD-275B
02-VCCW164 | VENT | 02-0.75"-CCW1205-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.2H |  | 3006 | PD-272B
02-VCCW165 | DRAIN | 02-0.75"-CCW1012-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3007 | PD-275B
02-VCCW166 | INSTRUMENTATION | 02-0.75"-CCW1021-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3008 | PD-275B
02-VCCW167 | ACHE OUTLET ISOLATION/THROTTLING | 02-12"-CCW1167-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 3009 | PD-271B
02-VCCW168 | DRAIN | 02-0.75"-CCW1229-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3010 | PD-272B
02-VCCW169 | INSTRUMENTATION | 02-0.75"-CCW1012-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3011 | PD-275B
02-VCCW170 | ACHE OUTLET ISOLATION/THROTTLING | 02-12"-CCW1170-1BAB2A | 12" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-STD |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 3012 | PD-271B
02-VCCW171 | INSTRUMENTATION | 02-0.75"-CCW1125-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3013 | PD-271B
02-VCCW172 | BFP SUPPLY ISOLATION | 02-3"-CCW1205-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 3014 | PD-272B
02-VCCW173 | INSTRUMENTATION | 02-0.75"-CCW1206-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3015 | PD-272B
02-VCCW174 | INSTRUMENTATION | 02-0.75"-CCW1108-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3016 | PD-271B
02-VCCW175 | SAMPLE PANEL FLOW THROTTLING | 02-4"-CCW1206-1BAB2A | 4" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 3017 | PD-272B
02-VCCW176 | VENT | 02-0.75"-CCW1225-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3018 | PD-272B
02-VCCW177 | BFP SUPPLY ISOLATION | 02-3"-CCW1211-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 3019 | PD-272B
02-VCCW178 | DRAIN | 02-0.75"-CCW1211-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3020 | PD-272B
02-VCCW179 | INSTRUMENTATION | 02-0.75"-CCW1226-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3021 | PD-272B
02-VCCW180 | INSTRUMENTATION | 02-0.75"-CCW1225-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3022 | PD-272B
02-VCCW181 | BFP FLOW THROTTLING | 02-3"-CCW1226-1BAB2A | 3" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 3023 | PD-272B
02-VCCW182 | BFP FLOW THROTTLING | 02-3"-CCW1225-1BAB2A | 3" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 3024 | PD-272B
02-VCCW183 | SAMPLE PANEL SUPPLY ISOLATION | 02-4"-CCW1229-1BAB2A | 4" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3025 | PD-272B
02-VCCW184 | VENT | 02-0.75"-CCW1206-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3026 | PD-272B
02-VCCW185 | TCU RETURN ISOLATION | 02-3"-CCW1010-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 3027 | PD-272B
02-VCCW186 | TCU SUPPLY ISOLATION | 02-3"-CCW1011-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 3028 | PD-272B
02-VCCW187 | INSTRUMENTATION | 02-0.75"-CCW1229-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3029 | PD-272B
02-VCCW188 | DRAIN | 02-0.75"-CCW1205-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3030 | PD-272B
02-VCCW189 | VENT | 02-0.75"-CCW1226-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3031 | PD-272B
02-VCCW190 | INSTRUMENTATION | 02-2"-CCW1017-1BCA3A-1.0 "MOH | 2" | Globe valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3032 | PD-270B
02-VCCW191 | INSTRUMENTATION | 02-2"-CCW1061-1BCA3A-1.0 "MOH | 2" | Globe valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3033 | PD-270B
02-VCCW192 | VENT | 02-0.75"-CCW1141-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 3034 | PD-270B
02-VCCW193 | VENT | 02-0.75"-CCW1141-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.2H |  | 3035 | PD-270B
02-VCCW194 | VENT | 02-0.75"-CCW1211-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.2H |  | 3036 | PD-272B
02-VCCW195 | DRAIN | 02-0.75"-CCW1031-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3037 | PD-275B
02-VCCW196 | DRAIN | 02-0.75"-CCW1000-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3038 | PD-270B
02-VCCW200 | VENT | 02-0.75"-CCW1101-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3039 | PD-270B
02-VCCW201 | VENT | 02-0.75"-CCW1103-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3040 | PD-270B
02-VCCW211 | INSTRUMENTATION | 02-0.75"-CCW1076-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3041 | PD-274B
02-VCCW212 | INSTRUMENTATION | 02-0.75"-CCW1032-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3042 | PD-274B
02-VCCW213 | INSTRUMENTATION | 02-0.75"-CCW1077-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3043 | PD-274B
02-VCCW214 | INSTRUMENTATION | 02-0.75"-CCW1078-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3044 | PD-274B
02-VCCW215 | INSTRUMENTATION | 02-0.75"-CCW1079-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3045 | PD-274B
02-VCCW216 | DRAIN | 02-0.75"-CCW1128-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3046 | PD-271B
02-VCCW217 | DRAIN | 02-0.75"-CCW1105-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3047 | PD-271B
02-VCCW218 | DRAIN | 02-0.75"-CCW1167-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3048 | PD-271B
02-VCCW219 | DRAIN | 02-0.75"-CCW1108-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3049 | PD-271B
02-VCCW220 | DRAIN | 02-0.75"-CCW1170-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3050 | PD-271B
02-VCCW221 | INSTRUMENTATION | 02-0.75"-CCW1075-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3051 | PD-274B
02-VCCW222 | INSTRUMENTATION | 02-0.75"-CCW1072-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3052 | PD-274B
02-VCCW224 | INSTRUMENTATION | 02-0.75"-CCW1073-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3053 | PD-274B
02-VCCW225 | INSTRUMENTATION | 02-0.75"-CCW1074-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3054 | PD-274B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3055 | P&ID
02-VCCW226 | DRAIN | 02-0.75"-CCW1142-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3056 | PD-271B
02-VCCW227 | DRAIN | 02-0.75"-CCW1145-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3057 | PD-271B
02-VCCW228 | DRAIN | 02-0.75"-CCW1123-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3058 | PD-271B
02-VCCW229 | DRAIN | 02-0.75"-CCW1160-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3059 | PD-271B
02-VCCW230 | DRAIN | 02-0.75"-CCW1120-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3060 | PD-271B
02-VCCW300 | INSTRUMENTATION | 02-0.75"-CCW1170-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3061 | PD-271B
02-VCCW301 | VENT | 02-0.75"-CCW1325-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.3H |  | 3062 | PD-273B
02-VCCW302 | VENT | 02-0.75"-CCW1332-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.3H |  | 3063 | PD-273B
02-VCCW304 | LUBE OIL MODULE SUPPLY ISOLATION | 02-14"-CCW1332-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 3064 | PD-273B
02-VCCW305 | LUBE OIL MODULE OUTLET ISOLATION/THROTTLING | 02-14"-CCW1305-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 3065 | PD-273B
02-VCCW306 | GLYCOL FILL CHECK | 02-2"-CCW1028-1BCA3A-1.0 "MOH | 2" | Check valve | CCW | 1BCA3A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 | PISTON | 3066 | PD-270B
02-VCCW307 | INSTRUMENTATION | 02-0.75"-CCW1020-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3067 | PD-273B
02-VCCW308 | DRAIN | 02-0.75"-CCW1020-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3068 | PD-273B
02-VCCW318 | DRAIN | 02-0.75"-CCW1334-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3069 | PD-274B
02-VCCW319 | DRAIN | 02-0.75"-CCW1335-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3070 | PD-274B
02-VCCW320 | GENERATOR COOLER SUPPLY ISOLATION | 02-6"-CCW1039-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3071 | PD-274B
02-VCCW321 | INSTRUMENTATION | 02-0.75"-CCW1039-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3072 | PD-274B
02-VCCW322 | DRAIN | 02-0.75"-CCW1305-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3073 | PD-273B
02-VCCW323 | INSTRUMENTATION | 02-0.75"-CCW1305-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3074 | PD-273B
02-VCCW324 | DRAIN | 02-0.75"-CCW1332-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3075 | PD-273B
02-VCCW325 | LUBE OIL MODULE SUPPLY ISOLATION | 02-14"-CCW1325-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 3076 | PD-273B
02-VCCW326 | DRAIN | 02-0.75"-CCW1325-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3077 | PD-273B
02-VCCW327 | INSTRUMENTATION | 02-0.75"-CCW1325-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.2H |  | 3078 | PD-273B
02-VCCW328 | VENT | 02-0.75"-CCW1325-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3079 | PD-273B
02-VCCW329 | INSTRUMENTATION | 02-0.75"-CCW1332-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3080 | PD-273B
02-VCCW330 | GENERATOR COOLER SUPPLY ISOLATION | 02-6"-CCW1038-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3081 | PD-274B
02-VCCW331 | INSTRUMENTATION | 02-0.75"-CCW1142-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3082 | PD-271B
02-VCCW332 | GENERATOR COOLER SUPPLY ISOLATION | 02-6"-CCW1037-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3083 | PD-274B
02-VCCW333 | INSTRUMENTATION | 02-0.75"-CCW1145-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3084 | PD-271B
02-VCCW334 | GENERATOR COOLER SUPPLY ISOLATION | 02-6"-CCW1036-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3085 | PD-274B
02-VCCW335 | INSTRUMENTATION | 02-0.75"-CCW1123-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3086 | PD-271B
02-VCCW336 | GENERATOR COOLER SUPPLY ISOLATION | 02-6"-CCW1035-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3087 | PD-274B
02-VCCW337 | INSTRUMENTATION | 02-0.75"-CCW1160-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3088 | PD-271B
02-VCCW338 | GENERATOR COOLER SUPPLY ISOLATION | 02-6"-CCW1034-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3089 | PD-274B
02-VCCW339 | INSTRUMENTATION | 02-0.75"-CCW1120-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3090 | PD-271B
02-VCCW340 | VENT | 02-0.75"-CCW1332-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3091 | PD-273B
02-VCCW341 | LUBE OIL MODULE OUTLET ISOLATION/THROTTLING | 02-14"-CCW1020-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 3092 | PD-273B
02-VCCW342 | GENERATOR COOLER SUPPLY ISOLATION | 02-6"-CCW1033-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3093 | PD-274B
02-VCCW343 | INSTRUMENTATION | 02-0.75"-CCW1033-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3094 | PD-274B
02-VCCW344 | GENERATOR COOLER SUPPLY ISOLATION | 02-6"-CCW1032-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-40 |  | No | 94.03.68.150.04.0 |  | 3095 | PD-274B
02-VCCW345 | GLYCOL FILL ISOLATION | 02-2"-CCW1028-1BCA3A-1.0 "MOH | 2" | Ball valve | CCW | 1BCA3A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3096 | PD-270B
02-VCCW346 | ECA COMPRESSOR RETURN ISOLATION | 02-3"-CCW1007-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 3097 | PD-275B
02-VCCW347 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 02-6"-CCW1079-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 3098 | PD-274B
02-VCCW348 | DRAIN | 02-0.75"-CCW1336-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3099 | PD-274B
02-VCCW349 | GENERATOR COOLER RETURN HEADER ISOLATION/THROTTLING | 02-14"-CCW1132-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-30 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE, GEAR OPERATOR | 3100 | PD-274B
02-VCCW350 | INSTRUMENTATION | 02-0.75"-CCW1038-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3101 | PD-274B
02-VCCW351 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 02-6"-CCW1078-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 3102 | PD-274B
02-VCCW352 | INSTRUMENTATION | 02-0.75"-CCW1037-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3103 | PD-274B
02-VCCW353 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 02-6"-CCW1077-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 3104 | PD-274B
02-VCCW354 | INSTRUMENTATION | 02-0.75"-CCW1036-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3105 | PD-274B
02-VCCW355 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 02-6"-CCW1076-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 3106 | PD-274B
02-VCCW356 | INSTRUMENTATION | 02-0.75"-CCW1035-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3107 | PD-274B
02-VCCW357 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 02-6"-CCW1075-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 3108 | PD-274B
02-VCCW358 | INSTRUMENTATION | 02-0.75"-CCW1034-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3109 | PD-274B
02-VCCW359 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 02-6"-CCW1074-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 3110 | PD-274B
02-VCCW360 | INSTRUMENTATION | 02-0.75"-CCW1007-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3111 | PD-275B
02-VCCW361 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 02-6"-CCW1073-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 3112 | PD-274B
02-VCCW362 | ECA COMPRESSOR SUPPLY ISOLATION | 02-3"-CCW1021-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 3113 | PD-275B
02-VCCW363 | GENERATOR COOLER RETURN ISOLATION/THROTTLING | 02-6"-CCW1072-1BAB2A | 6" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 | THROTTLING SERVICE | 3114 | PD-274B
02-VCCW364 | GENERATOR COOLER SUPPLY HEADER ISOLATION | 02-14"-CCW1662-1BAB2A | 14" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 135 | S-30 |  | No | 94.03.68.150.04.0 | GEAR OPERATOR | 3115 | PD-274B
02-VCCW365 | VENT | 02-0.75"-CCW1023-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3116 | PD-270B
02-VCCW366 | ACHE OUTLET HEADER ISOLATION | 02-24"-CCW1125-1BAB2A | 24" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | FFFE | FFFE | 150 | 135 | S-20 |  | No | 94.03.68.150.05.0 | GEAR OPERATOR | 3117 | PD-271B
02-VCCW367 | INSTRUMENTATION | 02-0.75"-CCW1044-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3118 | PD-270B
02-VCCW368 | INSTRUMENTATION | 02-0.75"-CCW1043-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3119 | PD-270B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3120 | P&ID
02-VCCW369 | ECA COMPRESSOR FLOW THROTTLING | 02-3"-CCW1007-1BAB2A | 3" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 | THROTTLING SERVICE | 3121 | PD-275B
02-VCCW370 | ECA COMPRESSOR RETURN ISOLATION | 02-3"-CCW1014-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 3122 | PD-275B
02-VCCW371 | DRAIN | 02-0.75"-CCW1337-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3123 | PD-274B
02-VCCW372 | DRAIN | 02-0.75"-CCW1052-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3124 | PD-274B
02-VCCW373 | DRAIN | 02-0.75"-CCW1053-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3125 | PD-274B
02-VCCW374 | DRAIN | 02-0.75"-CCW1054-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3126 | PD-274B
02-VCCW375 | DRAIN | 02-0.75"-CCW1055-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3127 | PD-274B
02-VCCW376 | DRAIN | 02-0.75"-CCW1056-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3128 | PD-274B
02-VCCW377 | DRAIN | 02-0.75"-CCW1057-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3129 | PD-274B
02-VCCW378 | DRAIN | 02-0.75"-CCW1058-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3130 | PD-274B
02-VCCW379 | DRAIN | 02-0.75"-CCW1059-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3131 | PD-274B
02-VCCW380 | ECA COMPRESSOR SUPPLY ISOLATION | 02-3"-CCW1001-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 135 | S-40 |  | No | 94.03.68.150.03.0 |  | 3132 | PD-275B
02-VCCW381 | ECA COMPRESSOR FLOW THROTTLING | 02-3"-CCW1014-1BAB2A | 3" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 3133 | PD-275B
02-VCCW382 | VENT | 02-0.75"-CCW1062-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3134 | PD-274B
02-VCCW383 | VENT | 02-0.75"-CCW1063-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3135 | PD-274B
02-VCCW384 | VENT | 02-0.75"-CCW1064-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3136 | PD-274B
02-VCCW385 | VENT | 02-0.75"-CCW1065-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3137 | PD-274B
02-VCCW386 | VENT | 02-0.75"-CCW1066-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3138 | PD-274B
02-VCCW387 | VENT | 02-0.75"-CCW1067-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3139 | PD-274B
02-VCCW388 | VENT | 02-0.75"-CCW1068-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3140 | PD-274B
02-VCCW389 | VENT | 02-0.75"-CCW1069-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3141 | PD-274B
02-VCCW391 | VENT | 02-0.75"-CCW1001-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3142 | PD-275B
02-VCCW392 | DRAIN | 02-0.75"-CCW1014-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3143 | PD-275B
02-VCCW393 | DRAIN | 02-0.75"-CCW1007-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3144 | PD-275B
02-VCCW396 | VENT | 02-0.75"-CCW1021-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3145 | PD-275B
02-VCCW398 | DRAIN | 02-0.75"-CCW1333-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3146 | PD-274B
02-VCCW399 | DRAIN | 02-0.75"-CCW1338-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3147 | PD-274B
02-VCCW400 | DRAIN | 02-0.75"-CCW1339-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3148 | PD-274B
02-VCCW401 | DRAIN | 02-0.75"-CCW1340-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3149 | PD-274B
02-VCCW402 | DRAIN | 02-0.75"-CCW1341-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3150 | PD-274B
02-VCCW403 | DRAIN | 02-0.75"-CCW1342-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3151 | PD-274B
02-VCCW404 | DRAIN | 02-0.75"-CCW1343-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3152 | PD-274B
02-VCCW405 | DRAIN | 02-0.75"-CCW1344-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3153 | PD-274B
02-VCCW406 | DRAIN | 02-0.75"-CCW1345-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3154 | PD-274B
02-VCCW407 | DRAIN | 02-0.75"-CCW1346-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3155 | PD-274B
02-VCCW408 | DRAIN | 02-0.75"-CCW1347-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3156 | PD-274B
02-VCCW409 | DRAIN | 02-0.75"-CCW1348-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3157 | PD-274B
02-VCCW410 | VENT | 02-0.75"-CCW1662-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3158 | PD-274B
02-VCCW411 | VENT | 02-0.75"-CCW1132-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 150 | S-80 |  | No | 94.03.68.150.06.0 |  | 3159 | PD-274B
02-VCCW412 | BFP RETURN ISOLATION | 02-3"-CCW1226-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 3160 | PD-272B
02-VCCW413 | BFP RETURN ISOLATION | 02-3"-CCW1225-1BAB2A | 3" | Gate valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | RFFE | RFFE | 150 | 150 | S-40 |  | No | 94.03.68.150.03.0 |  | 3161 | PD-272B
02-VCCW414 | TCU FILL ISOLATION | 02-0.75"-CCW1133-1BAB2A | 0.75" | Ball valve | CCW | 1BAB2A | WATER/GLYCOL | CL600 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3162 | PD-272B
02-VCCW415 | SAMPLE PANEL RETURN ISOLATION | 02-4"-CCW1206-1BAB2A | 4" | Butterfly valve | CCW | 1BAB2A | WATER/GLYCOL | CL150 | LUGGED | LUGGED | 150 | 150 | S-40 |  | No | 94.03.68.150.04.0 |  | 3163 | PD-272B
02-VCCW453 | INSTRUMENTATION | 02-0.75"-CCW1211-1BAB2A | 0.75" | Globe valve | CCW | 1BAB2A | WATER/GLYCOL | CL800 | SWE | SWE | 150 | 135 | S-80 |  | No | 94.03.68.150.06.0 |  | 3164 | PD-272B
02-VCMG202 | INSTRUMENTATION | 02-0.75"-CMG1016-1BCB6A | 0.75" | Globe valve | CMG | 1BCB6A | CARBON DIOXIDE | CL800 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 3165 | PD-571
02-VCMG203 | H2 ISOLATION | 02-1.5"-CMG1013-1BAA2A | 1.5" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 3166 | PD-571
02-VCMG206 | INSTRUMENTATION | 02-0.75"-CMG1102-1BCA1A | 0.75" | Globe valve | CMG | 1BCA1A | NITROGEN | CL800 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 3167 | PD-570
02-VCMG213 | H2 ISOLATION | 02-1.5"-CMG1013-1BAA2A | 1.5" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 3168 | PD-571
02-VCMG219 | INSTRUMENTATION | 02-0.75"-CMG1101-1BCA1A | 0.75" | Globe valve | CMG | 1BCA1A | NITROGEN | CL800 | SWE | SWE | 130 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 3169 | PD-570
02-VCMG222 | INSTRUMENTATION | 02-0.75"-CMG1010-1BCB6A | 0.75" | Globe valve | CMG | 1BCB6A | CARBON DIOXIDE | CL800 | SWE | SWE | 200 | 115 | S-40S |  | No | 94.03.68.150.06.0 |  | 3170 | PD-571
02-VCMG601 | VENT | 02-0.75"-CMG1013-1BAA2A | 0.75" | Globe valve | CMG | 1BAA2A | HYDROGEN | CL800 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 3171 | PD-571
02-VCMG603 | N2 PURGE CONNECTION | 02-0.75"-CMG1002-1BAA2A | 0.75" | Ball valve | CMG | 1BAA2A | HYDROGEN | CL600 | SWE | SWE | 150 | 115 | S-80 |  | No | 94.03.68.150.06.0 |  | 3172 | PD-571
02-VCND100 | STRAINER VENT VALVE | 02-0.5"-CND1074-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 3173 | PD-051B
02-VCND101 | IRON FILTER DRAIN | 02-0.75"-CND1056-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3174 | PD-052B
02-VCND103 | CONDENSATE EMERGENCY DUMP CV ISOLATION | 02-6"-CND1103-1EAA2A-1.0 "MOH | 6" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3175 | PD-053B
02-VCND104 | INSTRUMENT ISOLATION | 02-0.75"-CND1027-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3176 | PD-051B
02-VCND105 | CRH VENTILATOR SPRAY SUPPLY STRAINER ISOLATION | 02-0.75"-CND1415-1EAA1A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 790 | 310 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3177 | PD-040B
02-VCND106 | VENT VALVE | 02-0.75"-CND1050-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3178 | PD-050B
02-VCND108 | DRAIN VALVE | 02-0.75"-CND1062-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3179 | PD-030B
02-VCND109 | CRH VENTILATOR SPRAY SUPPLY ISOLATION | 02-3"-CND1062-1EAA2A-1.0 "MIC | 3" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.2H | FLEXIBLE WEDGE | 3180 | PD-030B
02-VCND110 | VENT VALVE | 02-0.75"-CND1062-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3181 | PD-030B
02-VCND111 | CRH VENTILATOR SPRAY SUPPLY CHECK VALVE | 02-3"-CND1092-1EBB1A-1.0 "EOH | 3" | Check valve | CND | 1EBB1A | Water | CL600 | BE | BE | 790 | 380 | S-40 | 1.0 " | Yes | 94.03.68.150.01.2H | SWING CHECK; FLOW: 25 GPM (MIN), 160 GPM (MAX) | 3182 | PD-030B
02-VCND112 | INSTRUMENT ISOLATION | 02-0.75"-CND1060-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3183 | PD-051B
02-VCND113 | CND PUMP CAN VENT VALVE | 02-1"-CND1131-1BAA2A-1.0 "MOH | 1" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3184 | PD-051B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3185 | P&ID
02-VCND114 | STRAINER DRAIN | 02-0.75"-CND1058-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3186 | PD-052B
02-VCND115 | LPS BYPASS SPRAY SUPPLY CHECK VALVE | 02-1.5"-CND1415-1EAA1A-1.0 "MOH | 1.5" | Check valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 790 | 310 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | PISTON CHECK; FLOW: 10 GPM (MIN), 40 GPM (MAX) | 3187 | PD-040B
02-VCND116 | DRAIN VALVE | 02-0.75"-CND1256-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3188 | PD-034B
02-VCND117 | CND PUMP DISCHARGE CHECK VALVE | 02-10"-CND1017-1EAA2A-1.0 "MOH | 10" | Check valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 500 GPM (MIN), 2000 GPM (MAX) | 3189 | PD-051B
02-VCND118 | DRAIN VALVE | 02-0.5"-CND1074-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 3190 | PD-051B
02-VCND119 | HRH BYPASS SPRAY SUPPLY ISOLATION | 02-6"-CND1256-1EAA2A-1.0 "MIC | 6" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3191 | PD-034B
02-VCND121 | HRH BYPASS SPRAY SUPPLY CHECK VALVE | 02-6"-CND1251-1EBB1A-1.5 "EOH | 6" | Check valve | CND | 1EBB1A | Water | CL600 | BE | BE | 790 | 380 | S-40 | 1.5 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 250 GPM (MIN), 850 GPM (MAX) | 3192 | PD-034B
02-VCND123 | INSTRUMENT ISOLATION | 02-0.75"-CND1002-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3193 | PD-052B
02-VCND124 | INSTRUMENT ISOLATION | 02-0.5"-CND1072-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3194 | PD-052B
02-VCND125 | INSTRUMENT ISOLATION | 02-0.5"-CND3317-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.2H |  | 3195 | PD-034B
02-VCND126 | ST HOOD SPRAY SUPPLY ISOLATION | 02-1.5"-CND1002-1EAA2A-1.0 "MIC | 1.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3196 | PD-052B
02-VCND127 | INSTRUMENT ISOLATION | 02-0.75"-CND1027-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3197 | PD-051B
02-VCND128 | CND PUMP DISCHARGE ISOLATION | 02-10"-CND1027-1EAA2A-1.0 "MOH | 10" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3198 | PD-051B
02-VCND129 | DRAIN VALVE | 02-0.5"-CND1075-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 3199 | PD-051B
02-VCND130 | INSTRUMENT ISOLATION | 02-0.75"-CND1017-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3200 | PD-051B
02-VCND131 | INSTRUMENT ISOLATION | 02-0.75"-CND1071-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3201 | PD-051B
02-VCND132 | CONDENSATE RECIRC CV DOWNSTREAM ISOLATION | 02-8"-CND1033-1EBB1A-1.0 "MOH | 8" | Ball valve | CND | 1EBB1A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.150.08.0 | FULL BORE, SURFACE HARDENED SEAT SUITABLE FOR TWO PHASE FLOW, RATED FOR VACUUM SERVICE, GEAR OPERATED, 12" OPERATOR MOUNTING KIT | 3202 | PD-053B
02-VCND133 | STRAINER VENT VALVE | 02-0.5"-CND1023-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3203 | PD-051B
02-VCND134 | CND TO ACC CURTAIN SPRAY FE ISOLATION | 02-4"-CND1038-1EAA2A-1.0 "MIC | 4" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3204 | PD-052B
02-VCND135 | STRAINER VENT VALVE | 02-0.5"-CND1075-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 3205 | PD-051B
02-VCND136 | DRAIN VALVE | 02-0.75"-CND1072-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3206 | PD-052B
02-VCND137 | INSTRUMENT ISOLATION | 02-0.75"-CND1094-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3207 | PD-051B
02-VCND138 | VENT VALVE | 02-0.75"-CND1072-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3208 | PD-052B
02-VCND139 | INSTRUMENT ISOLATION | 02-0.75"-CND1051-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3209 | PD-052B
02-VCND140 | IRON FILTER VENT VALVE | 02-0.75"-CND1052-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3210 | PD-052B
02-VCND141 | LPS BYPASS SPRAY SUPPLY ISOLATION | 02-1.5"-CND1459-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3211 | PD-040B
02-VCND142 | INSTRUMENT ISOLATION | 02-0.75"-CND1021-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3212 | PD-051B
02-VCND143 | INSTRUMENT ISOLATION | 02-0.75"-CND1021-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3213 | PD-051B
02-VCND144 | IRON FILTER DRAIN VALVE | 02-0.75"-CND1044-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3214 | PD-052B
02-VCND145 | ST HOOD SPRAY SUPPLY ISOLATION | 02-1.5"-CND1002-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H | WEDGE GATE | 3215 | PD-052B
02-VCND146 | INSTRUMENT ISOLATION | 02-0.75"-CND1072-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3216 | PD-052B
02-VCND147 | ST HOOD SPRAY BYPASS VALVE | 02-1.5"-CND1043-1EAA2A-1.0 "MIC | 1.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3217 | PD-052B
02-VCND148 | CND PUMP DISCHARGE CHECK VALVE | 02-10"-CND1027-1EAA2A-1.0 "MOH | 10" | Check valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 500 GPM (MIN), 2000 GPM (MAX) | 3218 | PD-051B
02-VCND149 | VENT VALVE | 02-0.75"-CND1189-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 3219 | PD-053B
02-VCND150 | CND DISCHARGE SAMPLE ISOLATION | 02-0.5"-CND1029-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3220 | PD-053B
02-VCND151 | INSTRUMENT ISOLATION | 02-0.75"-CND1027-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3221 | PD-052B
02-VCND152 | DRAIN VALVE | 02-0.75"-CND1033-1EBB1A-1.0 "MOH | 0.75" | Gate valve | CND | 1EBB1A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3222 | PD-053B
02-VCND153 | DRAIN VALVE | 02-0.75"-CND1103-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3223 | PD-053B
02-VCND154 | STRAINER VENT VALVE | 02-0.5"-CND1054-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3224 | PD-051B
02-VCND155 | CND DISCHARGE SAMPLE ISOLATION | 02-0.5"-CND1026-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3225 | PD-053B
02-VCND156 | INSTRUMENT ISOLATION | 02-0.5"-CND1869-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3226 | PD-040B
02-VCND157 | CND PUMP CAN VENT VALVE | 02-1"-CND1030-1BAA2A-1.0 "MOH | 1" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3227 | PD-051B
02-VCND158 | DRAIN VALVE | 02-0.75"-CND1459-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3228 | PD-040B
02-VCND159 | INSTRUMENT ISOLATION | 02-0.5"-CND1889-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3229 | PD-030B
02-VCND160 | CONDENSATE IRON FILTER BYPASS VALVE ISOLATION | 02-12"-CND1088-1EAA2A-1.0 "MOH | 12" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3230 | PD-052B
02-VCND162 | INSTRUMENT ISOLATION | 02-0.5"-CND1888-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3231 | PD-030B
02-VCND163 | CONDENSATE IRON FILTER BYPASS VALVE ISOLATION | 02-12"-CND1088-1EAA2A-1.0 "MOH | 12" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3232 | PD-052B
02-VCND164 | INSTRUMENT ISOLATION | 02-0.75"-CND1070-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3233 | PD-051B
02-VCND165 | STRAINER VENT VALVE | 02-0.5"-CND1076-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 3234 | PD-051B
02-VCND166 | STRAINER DRAIN | 02-2"-CND1012-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE, TO BE RATED FOR VACUUM SERVICE | 3235 | PD-051B
02-VCND167 | DRAIN VALVE | 02-0.75"-CND1094-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3236 | PD-051B
02-VCND168 | STRAINER VENT VALVE | 02-0.5"-CND1076-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H |  | 3237 | PD-051B
02-VCND169 | INSTRUMENT ISOLATION | 02-0.5"-CND1868-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3238 | PD-040B
02-VCND170 | INSTRUMENT ISOLATION | 02-0.5"-CND3321-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.2H |  | 3239 | PD-034B
02-VCND171 | STRAINER DRAIN | 02-2"-CND1067-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H | WEDGE GATE | 3240 | PD-051B
02-VCND172 | CONDENSATE IRON FILTER MANUAL ISOLATION | 02-12"-CND1001-1EAA2A-1.0 "MOH | 12" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3241 | PD-052B
02-VCND173 | STRAINER DRAIN | 02-2"-CND1073-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE, TO BE RATED FOR VACUUM SERVICE | 3242 | PD-051B
02-VCND174 | CONDENSATE IRON FILTER MANUAL ISOLATION | 02-12"-CND1000-1EAA2A-1.0 "MOH | 12" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3243 | PD-052B
02-VCND175 | INSTRUMENT ISOLATION | 02-0.5"-CND1072-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3244 | PD-052B
02-VCND176 | STRAINER DRAIN | 02-2"-CND1068-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H | WEDGE GATE | 3245 | PD-051B
02-VCND177 | IRON FILTER VENT | 02-0.75"-CND1089-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3246 | PD-052B
02-VCND178 | STRAINER DRAIN | 02-2"-CND1069-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.2H | WEDGE GATE | 3247 | PD-051B
02-VCND179 | INSTRUMENT ISOLATION | 02-0.75"-CND1010-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3248 | PD-051B
02-VCND180 | INSTRUMENT ISOLATION | 02-0.75"-CND1079-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3249 | PD-052B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3250 | P&ID
02-VCND181 | INSTRUMENT ISOLATION | 02-0.75"-CND1015-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3251 | PD-051B
02-VCND182 | VENT VALVE | 02-2"-CND1042-1EAA2A-1.0 "MOH | 2" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H | WEDGE GATE | 3252 | PD-052B
02-VCND183 | INSTRUMENT ISOLATION | 02-0.75"-CND1070-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3253 | PD-051B
02-VCND184 | INSTRUMENT ISOLATION | 02-0.75"-CND1087-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3254 | PD-052B
02-VCND185 | CND PUMP DISCHARGE CHECK VALVE | 02-10"-CND1094-1EAA2A-1.0 "MOH | 10" | Check valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 500 GPM (MIN), 2000 GPM (MAX) | 3255 | PD-051B
02-VCND186 | VENT VALVE | 02-0.75"-CND1002-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3256 | PD-052B
02-VCND187 | INSTRUMENT ISOLATION | 02-0.75"-CND1077-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3257 | PD-052B
02-VCND188 | DRAIN VALVE | 02-0.75"-CND1088-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3258 | PD-052B
02-VCND189 | DRAIN VALVE | 02-0.75"-CND1017-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3259 | PD-051B
02-VCND190 | INSTRUMENT ISOLATION | 02-0.5"-CND1072-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3260 | PD-052B
02-VCND191 | STRAINER VENT | 02-0.5"-CND1024-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3261 | PD-051B
02-VCND192 | INSTRUMENT ISOLATION | 02-0.75"-CND1071-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3262 | PD-051B
02-VCND193 | INSTRUMENT ISOLATION | 02-0.75"-CND1185-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3263 | PD-052B
02-VCND194 | CND PUMP DISCHARGE ISOLATION | 02-10"-CND1094-1EAA2A-1.0 "MOH | 10" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3264 | PD-051B
02-VCND195 | DRAIN VALVE | 02-0.75"-CND1098-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3265 | PD-053B
02-VCND196 | DRAIN VALVE | 02-0.75"-CND1027-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3266 | PD-051B
02-VCND197 | DRAIN VALVE | 02-0.75"-CND1259-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 3267 | PD-054B
02-VCND198 | HP DRAINS TANK QUENCH SPRAY VALVE ISOLATION | 02-3"-CND1202-1EAA2A-1.0 "MOH | 3" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3268 | PD-304B
02-VCND200 | DRAIN VALVE | 02-0.75"-CND1202-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3269 | PD-304B
02-VCND201 | GLAND STEAM DSH SPRAY ISOLATION | 02-1"-CND1181-1EAA2A-1.0 "MIC | 1" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3270 | PD-300B
02-VCND207 | VENT VALVE | 02-0.5"-CND1181-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3271 | PD-300B
02-VCND209 | VENT VALVE | 02-0.5"-CND1181-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3272 | PD-300B
02-VCND210 | VENT VALVE | 02-0.75"-CND1243-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3273 | PD-054B
02-VCND211 | DRAIN VALVE | 02-0.75"-CND1927-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3274 | PD-300B
02-VCND212 | GLAND STEAM DSH SPRAY SUPPLY ISOLATION | 02-1"-CND1181-1EAA2A-1.0 "MIC | 1" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3275 | PD-300B
02-VCND213 | GLAND STEAM DSH SPRAY CHECK | 02-1"-CND1928-1EAA1A-1.0 "MIC | 1" | Check valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 790 | 310 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | PISTON CHECK; FLOW: 10 GPM (MIN), 50 GPM (MAX) | 3276 | PD-300B
02-VCND214 | LP DRAINS TANK SPRAY SUPPLY CV ISOLATION | 02-2.5"-CND1200-1EAA2A-1.0 "MOH | 2.5" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3277 | PD-305B
02-VCND215 | DRAIN VALVE | 02-0.75"-CND1288-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3278 | PD-305B
02-VCND221 | LP BYPASS SPRAY SUPPLY ISOLATION | 02-1.5"-CND1459-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3279 | PD-052B
02-VCND223 | CND TO CRH VENTILATOR SPRAY ISOLATION | 02-3"-CND1062-1EAA2A-1.0 "MIC | 3" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.2H | FLEXIBLE WEDGE | 3280 | PD-052B
02-VCND224 | HRH BYPASS SPRAY SUPPLY ISOLATION | 02-6"-CND1256-1EAA2A-1.0 "MIC | 6" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3281 | PD-052B
02-VCND225 | CND STRAINER ISOLATION | 02-8"-CND1256-1EAA2A-1.0 "MIC | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3282 | PD-052B
02-VCND226 | STRAINER DRAIN | 02-1.5"-CND1046-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3283 | PD-052B
02-VCND227 | CND STRAINER ISOLATION | 02-8"-CND1256-1EAA2A-1.0 "MIC | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3284 | PD-052B
02-VCND228 | CND STRAINER ISOLATION | 02-8"-CND1266-1EAA2A-1.0 "MIC | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3285 | PD-052B
02-VCND229 | STRAINER DRAIN VALVE | 02-1.5"-CND1048-1EAA2A-1.0 "MIC | 1.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3286 | PD-052B
02-VCND230 | CND STRAINER ISOLATION | 02-8"-CND1266-1EAA2A-1.0 "MIC | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3287 | PD-052B
02-VCND231 | STRAINER VENT VALVE | 02-1.5"-CND1045-1EAA2A-1.0 "MIC | 1.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3288 | PD-052B
02-VCND232 | STRAINER VENT VALVE | 02-1.5"-CND1047-1EAA2A-1.0 "MIC | 1.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3289 | PD-052B
02-VCND233 | INSTRUMENT ISOLATION | 02-0.75"-CND1061-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3290 | PD-052B
02-VCND234 | INSTRUMENT ISOLATION | 02-0.75"-CND1061-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3291 | PD-052B
02-VCND235 | DEMIN FILL TO CND CHECK | 02-3"-CND1005-1ECA2A-1.0 "MOH | 3" | Check valve | CND | 1ECA2A | Water | CL600 | BE | BE | 790 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 100-250 GPM | 3292 | PD-052B
02-VCND236 | DEMIN FILL TO CND STOP CHECK | 02-3"-CND1005-1ECA2A-1.0 "MOH | 3" | Check Valve Locked Closed | CND | 1ECA2A | Water | CL600 | BE | BE | 790 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.01.1H | GLOBE STOP-CHECK; FLOW: 100-250 GPM | 3293 | PD-052B
02-VCND237 | DRAIN/HYDRO FILL VALVE | 02-0.75"-CND1005-1ECA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1ECA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-40S | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3294 | PD-052B
02-VCND238 | DEMIN FILL TO CND ISOLATION | 02-3"-CND1005-1ECA2A-1.0 "MOH | 3" | Globe valve | CND | 1ECA2A | Water | CL600 | BE | BE | 790 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.01.1H |  | 3295 | PD-052B
02-VCND239 | ECA COOLER PUMP DISCHARGE CHECK | 02-6"-CND1235-1EAA1A-1.0 "EOH | 6" | Check valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 100 GPM (MIN), 500 GPM (MAX) | 3296 | PD-054B
02-VCND240 | INSTRUMENT ISOLATION | 02-0.75"-CND1243-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3297 | PD-054B
02-VCND241 | ECA COOLER PUMP DISCHARGE CHECK | 02-6"-CND1259-1EAA1A-1.0 "EOH | 6" | Check valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 100 GPM (MIN), 500 GPM (MAX) | 3298 | PD-054B
02-VCND242 | ECA COOLING LOOP SUPPLY CHECK | 02-6"-CND1031-1EAA1A-1.0 "EOH | 6" | Check valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | TILTING DISC; FLOW: 100 GPM (MIN), 500 GPM (MAX) | 3299 | PD-054B
02-VCND243 | ECA COOLING LOOP MANUAL FLOW THROTTLING VALVE | 02-6"-CND1263-1EAA1A-1.0 "EOH | 6" | Globe valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H |  | 3300 | PD-054B
02-VCND244 | STEAM DRAINS PUMP SEAL WATER SUPPLY ISOLATION | 02-0.5"-CND1109-1BAA2A-1.0 "MOH | 0.5" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 3301 | PD-306B
02-VCND245 | STEAM DRAINS PUMP SEAL WATER SUPPLY THROTTLING VALVE | 02-0.5"-CND1109-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3302 | PD-306B
02-VCND247 | INSTRUMENT ISOLATION | 02-0.5"-CND1109-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3303 | PD-306B
02-VCND248 | STEAM DRAINS PUMP SEAL WATER SUPPLY CHECK | 02-0.5"-CND1109-1BAA2A-1.0 "MOH | 0.5" | Check valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | BALL CHECK; FLOW: 1-2 GPM | 3304 | PD-306B
02-VCND258 | VENT VALVE | 02-0.75"-CND1050-1BAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3305 | PD-050B
02-VCND259 | DRAIN VALVE | 02-0.75"-CND1050-1BAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3306 | PD-050B
02-VCND260 | DRAIN VALVE | 02-0.75"-CND1251-1EBB1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EBB1A | Water | CL800 | SWE | SWE | 790 | 380 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3307 | PD-034B
02-VCND261 | LP DRAINS TANK QUENCH TCV ISOLATION | 02-2.5"-CND1200-1EAA2A-1.0 "MOH | 2.5" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3308 | PD-305B
02-VCND262 | LP DRAINS TANK QUENCH TCV BYPASS VALVE | 02-2"-CND1201-1EAA2A-1.0 "MOH | 2" | Globe valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 3309 | PD-305B
02-VCND271 | STRAINER DRAIN | 02-0.5"-CND1002-1EAA2A-1.0 "MIC | 0.5" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H | WEDGE GATE | 3310 | PD-052B
02-VCND272 | STEAM DRAINS PUMP SEAL WATER SUPPLY THROTTLING VALVE | 02-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3311 | PD-306B
02-VCND273 | VENT VALVE | 02-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3312 | PD-306B
02-VCND274 | INSTRUMENT ISOLATION | 02-0.5"-CND1040-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3313 | PD-306B
02-VCND275 | INSTRUMENT ISOLATION | 02-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3314 | PD-306B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3315 | P&ID
02-VCND277 | STEAM DRAINS PUMP SEAL WATER SUPPLY CHECK | 02-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Check valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | BALL CHECK; FLOW: 1-2 GPM | 3316 | PD-306B
02-VCND278 | INSTRUMENT ISOLATION | 02-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3317 | PD-306B
02-VCND279 | STEAM DRAINS PUMP SEAL WATER SUPPLY THROTTLING VALVE | 02-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3318 | PD-306B
02-VCND280 | STEAM DRAINS PUMP SEAL WATER SUPPLY ISOLATION | 02-0.5"-CND1009-1BAA2A-1.0 "MOH | 0.5" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 150 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 3319 | PD-306B
02-VCND301 | INSTRUMENT ISOLATION | 02-0.5"-CND1256-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3320 | PD-034B
02-VCND302 | INSTRUMENT ISOLATION | 02-0.5"-CND1014-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3321 | PD-034B
02-VCND307 | VENT VALVE | 02-0.75"-CND1258-1EAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3322 | PD-034B
02-VCND308 | INSTRUMENT ISOLATION | 02-0.5"-CND1072-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3323 | PD-052B
02-VCND309 | LP ECONOMIZER BYPASS CV ISOLATION | 02-8"-CND1020-1EAA2A-1.0 "MOH | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3324 | PD-053B
02-VCND311 | ECA COOLER PUMP SUCTION ISOLATION | 02-6"-CND1031-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3325 | PD-054B
02-VCND312 | INSTRUMENT ISOLATION | 02-0.75"-CND1233-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3326 | PD-054B
02-VCND313 | ECA COOLER PUMP SUCTION ISOLATION | 02-6"-CND1233-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3327 | PD-054B
02-VCND314 | ECA COOLER PUMP DISCHARGE ISOLATION | 02-6"-CND1235-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3328 | PD-054B
02-VCND315 | INSTRUMENT ISOLATION | 02-0.75"-CND1235-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3329 | PD-054B
02-VCND320 | STRAINER VENT VALVE | 02-0.5"-CND1024-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3330 | PD-051B
02-VCND321 | INSTRUMENT ISOLATION | 02-0.5"-CND1152-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3331 | PD-052B
02-VCND322 | INSTRUMENT ISOLATION | 02-0.5"-CND1149-1EAA2A-1.0 "MIC | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3332 | PD-052B
02-VCND323 | CONDENSATE RECIRC STRAINER ISOLATION | 02-8"-CND1161-1EAA2A-1.0 "MOH | 8" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3333 | PD-053B
02-VCND324 | ACC CURTAIN SPRAY CV ISOLATION | 02-4"-CND1038-1EAA2A-1.0 "MIC | 4" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3334 | PD-052B
02-VCND326 | ACC CURTAIN SPRAY CV ISOLATION | 02-4"-CND1038-1EAA2A-1.0 "MIC | 4" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3335 | PD-052B
02-VCND327 | ACC CURTAIN SPRAY CV BYPASS VALVE | 02-2"-CND1382-1EAA2A-1.0 "MIC | 2" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3336 | PD-052B
02-VCND328 | INSTRUMENT ISOLATION | 02-0.75"-CND1096-1DAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1DAA2A | Water | CL800 | SWE | SWE | 475 | 170 | S-80 | 1.0 " | No | 94.03.68.150.02.1H |  | 3337 | PD-052B
02-VCND329 | CONDENSATE PUMP DISCHARGE ISOLATION | 02-10"-CND1017-1EAA2A-1.0 "MOH | 10" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3338 | PD-051B
02-VCND330 | STRAINER VENT VALVE | 02-0.5"-CND1023-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3339 | PD-051B
02-VCND333 | CND PUMP VENT VALVE | 02-1"-CND1022-1BAA2A-1.0 "MOH | 1" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3340 | PD-051B
02-VCND335 | INSTRUMENT ISOLATION | 02-0.75"-CND1259-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3341 | PD-054B
02-VCND337 | INSTRUMENT ISOLATION | 02-0.75"-CND1188-1DAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1DAA2A | Water | CL800 | SWE | SWE | 600 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3342 | PD-053B
02-VCND338 | INSTRUMENT ISOLATION | 02-0.75"-CND1188-1DAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1DAA2A | Water | CL800 | SWE | SWE | 600 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3343 | PD-053B
02-VCND339 | INSTRUMENT ISOLATION | 02-0.75"-CND1187-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3344 | PD-053B
02-VCND340 | ECA COOLER LOOP RETURN VALVE ISOLATION | 02-6"-CND1039-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3345 | PD-054B
02-VCND341 | DRAIN VALVE | 02-0.75"-CND1243-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3346 | PD-054B
02-VCND342 | INSTRUMENT ISOLATION | 02-0.75"-CND1259-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3347 | PD-054B
02-VCND343 | ECA COOLER LOOP RETURN VALVE ISOLATION | 02-6"-CND1039-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3348 | PD-054B
02-VCND344 | INSTRUMENT ISOLATION | 02-0.75"-CND1263-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3349 | PD-054B
02-VCND348 | DRAIN VALVE | 02-0.75"-CND1039-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3350 | PD-054B
02-VCND349 | DRAIN VALVE | 02-0.75"-CND1031-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3351 | PD-054B
02-VCND352 | ECA COOLER LOOP SUPPLY VALVE ISOLATION | 02-6"-CND1031-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3352 | PD-054B
02-VCND357 | INSTRUMENT ISOLATION | 02-0.75"-CND1031-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3353 | PD-054B
02-VCND359 | ECA COOLER PUMP DISCHARGE ISOLATION | 02-6"-CND1259-1EAA1A-1.0 "EOH | 6" | Gate valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3354 | PD-054B
02-VCND360 | STRAINER VENT VALVE | 02-0.5"-CND1054-1BAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | TO BE RATED FOR VACUUM SERVICE | 3355 | PD-051B
02-VCND361 | STRAINER DRAIN VALVE | 02-2"-CND1016-1BAA2A-1.0 "MOH | 2" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE, TO BE RATED FOR VACUUM SERVICE | 3356 | PD-051B
02-VCND362 | IRON FILTER DRAIN VALVE | 02-0.75"-CND1064-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3357 | PD-052B
02-VCND363 | DRAIN VALVE | 02-0.75"-CND1092-1EBB1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EBB1A | Water | CL800 | SWE | SWE | 790 | 380 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H | WEDGE GATE | 3358 | PD-030B
02-VCND366 | HP DRAINS TANK QUENCH TCV BYPASS VALVE | 02-1.5"-CND1049-1EAA2A-1.0 "MOH | 1.5" | Globe valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 3359 | PD-304B
02-VCND367 | HP DRAINS TANK QUENCH TCV ISOLATION | 02-3"-CND1202-1EAA2A-1.0 "MOH | 3" | Gate valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.01.1H | FLEXIBLE WEDGE | 3360 | PD-304B
02-VCND375 | INSTRUMENT ISOLATION | 02-0.75"-CND1187-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.1H |  | 3361 | PD-053B
02-VCND376 | VENT VALVE | 02-0.75"-CND1168-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 3362 | PD-053B
02-VCND377 | DRAIN VALVE | 02-0.75"-CND1161-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0 | WEDGE GATE | 3363 | PD-053B
02-VCND378 | VENT VALVE | 02-0.75"-CND1033-1EBB1A-1.0 "MOH | 0.75" | Globe valve | CND | 1EBB1A | Water | CL1500 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 3364 | PD-053B
02-VCND379 | VENT VALVE | 02-0.75"-CND1161-1EAA2A-1.0 "MOH | 0.75" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 3365 | PD-053B
02-VCND380 | DRAIN VALVE | 02-0.75"-CND1258-1EAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.0 | WEDGE GATE | 3366 | PD-034B
02-VCND381 | VENT VALVE | 02-0.75"-CND1251-1EBB1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EBB1A | Water | CL1500 | SWE | SWE | 790 | 380 | S-80 | 1.0 " | Yes | 94.03.68.150.02.2H |  | 3367 | PD-034B
02-VCND400 | VENT VALVE | 02-1"-CND1055-1EAA2A-1.0 "MIC | 1" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3368 | PD-052B
02-VCND401 | VENT | 02-1"-CND1078-1EAA2A-1.0 "MIC | 1" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3369 | PD-052B
02-VCND402 | DRAIN VALVE | 02-1"-CND1081-1EAA2A-1.0 "MIC | 1" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H | WEDGE GATE | 3370 | PD-052B
02-VCND403 | DRAIN VALVE | 02-1"-CND1084-1EAA2A-1.0 "MIC | 1" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H | WEDGE GATE | 3371 | PD-052B
02-VCND404 | VENT VALVE | 02-0.5"-CND1097-1EAA2A-1.0 "MOH | 0.5" | Globe valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 290 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 3372 | PD-053B
02-VCND405 | VENT VALVE | 02-0.75"-CND1096-1DAA2A-1.0 "MIC | 0.75" | Globe valve | CND | 1DAA2A | Water | CL800 | SWE | SWE | 475 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H |  | 3373 | PD-053B
02-VCND406 | STRAINER DRAIN VALVE | 02-0.75"-CND1181-1EAA2A-1.0 "MIC | 0.75" | Gate valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.150.06.3H | WEDGE GATE | 3374 | PD-300B
02-VCND407 | VENT VALVE | 02-0.75"-CND1263-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 3375 | PD-054B
02-VCND408 | DRAIN VALVE | 02-0.75"-CND1263-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | WEDGE GATE | 3376 | PD-054B
02-VCND410 | VENT VALVE | 02-0.75"-CND1031-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 3377 | PD-054B
02-VCND411 | VENT VALVE | 02-0.75"-CND1259-1EAA1A-1.0 "EOH | 0.75" | Globe valve | CND | 1EAA1A | Water | CL800 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 3378 | PD-054B
02-VCND420 | ECA COOLER PUMP DRAIN | 02-0.75"-CND1116-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL2500 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.03.3 |  | 3379 | PD-054B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3380 | P&ID
02-VCND421 | ECA COOLER PUMP DRAIN | 02-0.75"-CND1114-1EAA1A-1.0 "EOH | 0.75" | Gate valve | CND | 1EAA1A | Water | CL2500 | SWE | SWE | 850 | 302 | S-80 | 1.0 " | Yes | 94.03.68.150.03.3 |  | 3381 | PD-054B
02-VCND576 | DRAIN VALVE | 02-0.75"-CND1892-1BAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 3382 | PD-053B
02-VCND577 | DRAIN | 02-0.75"-CND1890-1BAA2A-1.0 "MOH | 0.75" | Gate valve | CND | 1BAA2A | Water | CL800 | SWE | SWE | 50 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | WEDGE GATE | 3383 | PD-053B
02-VCRH101 | CRH TO AXS BLOCK/CONTROL VALVE DRAIN VALVE | 02-0.75"-CRH1044-1EBB1A-2.5 "EIC | 0.75" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3384 | PD-030B
02-VCRH102 | PIT CONNECTION ROOT VALVE | 02-0.75"-CRH1101-1EBA1A-2.0 "EOH | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL1500 | SWE | SWE | 150 | 950 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3385 | PD-030B
02-VCRH103 | PIT CONNECTION BLOCK VALVE | 02-0.75"-CRH1101-1EBA1A-2.0 "EOH | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL1500 | SWE | SWE | 150 | 950 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3386 | PD-030B
02-VCRH104 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1049-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3387 | PD-030B
02-VCRH105 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1053-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3388 | PD-030B
02-VCRH106 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1052-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3389 | PD-030B
02-VCRH107 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1048-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3390 | PD-030B
02-VCRH108 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1046-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3391 | PD-030B
02-VCRH109 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1045-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3392 | PD-030B
02-VCRH110 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1047-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3393 | PD-030B
02-VCRH111 | DRIP LEG DRAIN | 02-2"-CRH1004-1EBA1A-2.0 "EOH | 2" | Ball valve | CRH | 1EBA1A | Steam | CL600 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 3394 | PD-031B
02-VCRH112 | DRIP LEG LS VENT/DRAIN VALVE | 02-1"-CRH1044-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3395 | PD-030B
02-VCRH115 | HYDRO/VENT CONNECTION VALVE | 02-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3396 | PD-031B
02-VCRH117 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1058-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3397 | PD-031B
02-VCRH120 | CRH TO AXS VENT VALVE | 02-0.75"-CRH1162-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3398 | PD-124B
02-VCRH121 | CRH TO AXS VENT VALVE | 02-0.75"-CRH1162-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3399 | PD-124B
02-VCRH122 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1057-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3400 | PD-031B
02-VCRH123 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1053-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3401 | PD-030B
02-VCRH124 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1057-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3402 | PD-031B
02-VCRH125 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1045-1EBB1A-2.5 "EIC | 0.75" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3403 | PD-030B
02-VCRH127 | DRIP LEG DRAIN | 02-2"-CRH1025-1EBB1A-3.5 "EIC | 2" | Ball valve | CRH | 1EBB1A | Steam | CL600 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 3404 | PD-030B
02-VCRH128 | PIT CONNECTION BLOCK VALVE | 02-0.75"-CRH1042-1EBB1A-2.5 "EIC | 0.75" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3405 | PD-030B
02-VCRH130 | DRIP LEG DRAIN | 02-2"-CRH1026-1EBA1A-2.0 "EOH | 2" | Ball valve | CRH | 1EBA1A | Steam | CL600 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 3406 | PD-030B
02-VCRH131 | VENTILATOR VALVE BLOCK VALVE | 02-10"-CRH1142-1EBB1A-4.5 "EIC | 10" | Gate valve | CRH | 1EBB1A | Steam | CL600 | BE | BE | 630 | 950 | S-60 | 4.5 " | No | 94.03.68.150.01.0H | PARALLEL SLIDE DISC, EXTERNAL BONNET DRAIN | 3407 | PD-030B
02-VCRH133 | DRIP LEG DRAIN VALVE | 02-2"-CRH1041-1EBB1A-3.5 "EIC | 2" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3408 | PD-030B
02-VCRH134 | DRIP LEG DRAIN VALVE | 02-2"-CRH1041-1EBB1A-3.5 "EIC | 2" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3409 | PD-030B
02-VCRH135 | DRIP LEG DRAIN VALVE | 02-2"-CRH1063-1EBA1A-2.0 "EOH | 2" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | - | 3410 | PD-030B
02-VCRH136 | DRIP LEG DRAIN VALVE | 02-2"-CRH1113-1EBA1A-2.0 "EOH | 2" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | - | 3411 | PD-031B
02-VCRH137 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1055-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3412 | PD-031B
02-VCRH138 | DRIP LEG DRAIN VALVE | 02-2"-CRH1063-1EBA1A-2.0 "EOH | 2" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | - | 3413 | PD-030B
02-VCRH139 | PTC CONNECTION | 02-0.75"-CRH1042-1EBB1A-3.5 "EIC | 0.75" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3414 | PD-030B
02-VCRH141 | PIT CONNECTION BLOCK VALVE | 02-0.75"-CRH1101-1EBA1A-2.0 "EOH | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL1500 | SWE | SWE | 150 | 950 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3415 | PD-030B
02-VCRH142 | PIT CONNECTION BLOCK VALVE | 02-0.75"-CRH1101-1EBA1A-2.0 "EOH | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL1500 | SWE | SWE | 150 | 950 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3416 | PD-030B
02-VCRH143 | PIT CONNECTION BLOCK VALVE | 02-0.75"-CRH1042-1EBB1A-2.5 "EIC | 0.75" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3417 | PD-030B
02-VCRH144 | PIT CONNECTION BLOCK VALVE | 02-0.75"-CRH1042-1EBB1A-3.5 "EIC | 0.75" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3418 | PD-030B
02-VCRH146 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1056-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3419 | PD-031B
02-VCRH147 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1056-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3420 | PD-031B
02-VCRH148 | PT CONNECTION ROOT VALVE | 02-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3421 | PD-031B
02-VCRH150 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1045-1EBB1A-2.5 "EIC | 0.75" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3422 | PD-030B
02-VCRH151 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1044-1EBB1A-2.5 "EIC | 0.75" | Gate valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3423 | PD-030B
02-VCRH154 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1052-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3424 | PD-030B
02-VCRH155 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1049-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3425 | PD-030B
02-VCRH156 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1048-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3426 | PD-030B
02-VCRH157 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1053-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3427 | PD-030B
02-VCRH158 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1048-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3428 | PD-030B
02-VCRH159 | HYDRO/VENT CONNECTION VALVE | 02-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3429 | PD-031B
02-VCRH160 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1048-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3430 | PD-030B
02-VCRH161 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1053-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3431 | PD-030B
02-VCRH162 | CRH TO AXS VENT VALVE | 02-0.75"-CRH1162-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3432 | PD-124B
02-VCRH165 | HYDRO/VENT CONNECTION VALVE | 02-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3433 | PD-031B
02-VCRH166 | FIT/FE ROOT VALVE | 02-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3434 | PD-031B
02-VCRH169 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1055-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3435 | PD-031B
02-VCRH170 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1058-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3436 | PD-031B
02-VCRH171 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1056-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3437 | PD-031B
02-VCRH172 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1057-1EBA1A-1.5 "EOH | 1" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3438 | PD-031B
02-VCRH173 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1056-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3439 | PD-031B
02-VCRH174 | DRIP LEG LS VENT/DRAIN VALVE | 02-0.75"-CRH1057-1EBA1A-1.5 "EOH | 0.75" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | - | 3440 | PD-031B
02-VCRH175 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1046-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3441 | PD-030B
02-VCRH176 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1047-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3442 | PD-030B
02-VCRH177 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1045-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3443 | PD-030B
02-VCRH178 | DRIP LEG LS ROOT VALVE | 02-1"-CRH1044-1EBB1A-3.0 "EIC | 1" | Globe valve | CRH | 1EBB1A | Steam | CL1500 | SWE | SWE | 630 | 950 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3444 | PD-030B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3445 | P&ID
02-VCRH180 | CRH TO AXS ISOLATION | 02-3"-CRH1193-1EBA1A-2.5 "EOC | 3" | Gate valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 2.5 " | No | 94.03.68.150.01.1H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 3446 | PD-124B
02-VCRH181 | CRH TO AXS ISOLATION | 02-4"-CRH1162-1EBA1A-2.5 "EOC | 4" | Gate valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 2.5 " | No | 94.03.68.150.01.1H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 3447 | PD-124B
02-VCRH182 | CRH TO AXS VENT VALVE | 02-0.75"-CRH1162-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3448 | PD-124B
02-VCRH183 | CRH TO AXS ISOLATION | 02-4"-CRH1193-1EBA1A-2.5 "EOC | 4" | Gate valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 2.5 " | No | 94.03.68.150.01.1H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 3449 | PD-124B
02-VCRH184 | CRH TO AXS ISOLATION | 02-6"-CRH1162-1EBA1A-3.0 "EOC | 6" | Gate valve | CRH | 1EBA1A | Steam | CL600 | BE | BE | 630 | 780 | S-40 | 3.0 " | No | 94.03.68.150.01.1H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 3450 | PD-124B
02-VCRH185 | DRIP LEG DRAIN | 02-2"-CRH1113-1EBA1A-2.0 "EOH | 2" | Gate valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 2.0 " | Yes | 94.03.68.150.02.0H | - | 3451 | PD-031B
02-VCRH186 | HYDRO/VENT CONNECTION VALVE | 02-0.75"-CRH1050-1EBA1A-1.5 "EOC | 0.75" | Globe valve | CRH | 1EBA1A | Steam | CL800 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3452 | PD-031B
02-VCTP101 | UNIT 2 ECA COOLER DRAIN VALVE (B) ISOLATION | 02-1"-CTP1041-1DAA1A-1.5 "EOI | 1" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 662 | S-80 | 1.5 " | No | 94.03.68.150.06.2H |  | 3453 | PD-335B
02-VCTP102 | DRAIN ISOLATION | 02-0.75"-CTP1083-1DBA1A-2.5 "EOH | 0.75" | Globe valve | CTP | 1DBA1A | Air/Water | CL800 | SWE | SWE | 74 | 1040 | S-80 | 2.5 " | Yes | 94.03.68.150.06.3H |  | 3454 | PD-336B
02-VCTP103 | UNIT 2 BLADE RING DRAIN ISOLATION | 02-2"-CTP1003-1EAA1A-1.0 "EOI | 2" | Gate valve | CTP | 1EAA1A | Air/Water | CL800 | SWE | SWE | 682 | 482 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 3455 | PD-335B
02-VCTP104 | UNIT 2 ECA DRAIN MIST DEPARATOR DRAIN VALVE (B) ISOLATION | 02-1"-CTP1042-1DAA1A-1.0 "EOI | 1" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 3456 | PD-335B
02-VCTP105 | UNIT 2 BLADE COMBUSTOR ISOLATION | 02-1"-CTP1005-1EAA1A-1.0 "EOI | 1" | Gate valve | CTP | 1EAA1A | Air/Water | CL800 | SWE | SWE | 682 | 482 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 3457 | PD-335B
02-VCTP106 | UNIT 2 ECA DRAIN MIST DEPARATOR DRAIN VALVE (A) ISOLATION | 02-2"-CTP1050-1DAA1A-1.0 "EOI | 2" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 3458 | PD-335B
02-VCTP107 | UNIT 2 ECA COOLER DRAIN VALVE (A) ISOLATION | 02-2"-CTP1077-1DAA1A-1.5 "EOI | 2" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 662 | S-80 | 1.5 " | No | 94.03.68.150.06.2H |  | 3459 | PD-335B
02-VCTP108 | UNIT 2 COOLING AIR COOLER (HIGH TEMP) DRAIN VALVE (B) ISOLATION | 02-1"-CTP1057-1DAA1A-1.5 "EOI | 1" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 752 | S-80 | 1.5 " | No | 94.03.68.150.06.2H |  | 3460 | PD-335B
02-VCTP109 | UNIT 2 COOLING AIR COOLER (HIGH TEMP) DRAIN VALVE (A) ISOLATION | 02-2"-CTP1073-1DAA1A-1.0 "EOI | 2" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 509 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 3461 | PD-335B
02-VCTP110 | UNIT 2 COOLING AIR COOLER (LOW TEMP) DRAIN VALVE (A) ISOLATION | 02-2"-CTP1046-1DAA1A-2.0 "EOI | 2" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 752 | S-80 | 2.0 " | No | 94.03.68.150.06.2H |  | 3462 | PD-335B
02-VCTP111 | UNIT 2 COOLING AIR COOLER (LOW TEMP) DRAIN VALVE (B) ISOLATION | 02-1"-CTP1071-1DAA1A-1.0 "EOI | 1" | Gate valve | CTP | 1DAA1A | Air/Water | CL800 | SWE | SWE | 406 | 509 | S-80 | 1.0 " | No | 94.03.68.150.06.2H |  | 3463 | PD-335B
02-VCTP113 | UNIT 2 2C COOLER DRAIN VALVE ISOLATION | 02-4"-CTP1091-1DBB1A-4.0 "EII | 4" | Gate valve | CTP | 1DBB1A | Air/Water | CL300 | BE | BE | 283 | 968 | S-40 | 4.0 " | No | 94.03.68.150.03.2H | DOUBLE DISK WEDGE, 3-WAY DRAIN | 3464 | PD-336B
02-VCTP114 | DRAIN ISOLATION | 02-0.75"-CTP1068-1BAA1A-1.0 "MII | 0.75" | Ball valve | CTP | 1BAA1A | AIR/OIL | CL600 | SWE | SWE | 15 | 194 | S-80 | 1.0 " | No | 94.03.68.150.06.1 |  | 3465 | PD-334B
02-VCTP115 | DRAIN ISOLATION | 02-0.75"-CTP1092-1BCA2A | 0.75" | Ball valve | CTP | 1BCA2A | AIR | CL600 | SWE | SWE | 145 | 212 | S-40S |  | No | 94.03.68.150.06.1 |  | 3466 | PD-336B
02-VCTP116 | DRAIN ISOLATION | 02-0.75"-CTP1066-1BCA2A | 0.75" | Ball valve | CTP | 1BCA2A | AIR | CL600 | SWE | SWE | 145 | 212 | S-40S |  | No | 94.03.68.150.06.1 |  | 3467 | PD-336B
02-VCTP117 | COOLING AIR TO FUEL GAS NOZZLE ISOLATION | 02-6"-CTP1066-1BCA2A | 6" | Butterfly valve | CTP | 1BCA2A | AIR | CL150 | LUGGED | LUGGED | 145 | 212 | S-10S |  | No | 94.03.68.150.04.2 | INDOOR INSTALLATION PER PIPE ROUTING, PROVIDE 20 FT CHAIN WHEEL OPERATOR | 3468 | PD-336B
02-VCTP120 | DRAIN ISOLATION | 02-0.75"-CTP1004-1BAA1A-1.0 "MII | 0.75" | Ball valve | CTP | 1BAA1A | AIR/OIL | CL600 | SWE | SWE | 15 | 194 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 3469 | PD-334B
02-VCTP146 | DRAIN ISOLATION | 02-0.75"-CTP1081-1DBA1A-2.5 "EOH | 0.75" | Globe valve | CTP | 1DBA1A | Air/Water | CL800 | SWE | SWE | 74 | 1040 | S-80 | 2.5 " | Yes | 94.03.68.150.06.3H |  | 3470 | PD-336B
02-VCTP179 | DRAIN ISOLATION | 02-0.75"-CTP1070-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 3471 | PD-333B
02-VCTP180 | DRAIN ISOLATION | 02-0.75"-CTP1049-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 3472 | PD-333B
02-VCTP181 | DRAIN ISOLATION | 02-0.75"-CTP1019-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 3473 | PD-333B
02-VCTP182 | DRAIN ISOLATION | 02-0.75"-CTP1029-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 3474 | PD-333B
02-VCTP183 | DRAIN ISOLATION | 02-0.75"-CTP1039-1BCA1A-1.0 "MOH | 0.75" | Ball valve | CTP | 1BCA1A | Water | CL600 | SWE | SWE | 15 | 102 | S-40S | 1.0 " | Yes | 94.03.68.150.06.1 |  | 3475 | PD-333B
02-VCTP185 | INSTRUMENT ISOLATION | 02-0.75"-CTP1060-1BCA2A-1.0 "MOH | 0.75" | Globe valve | CTP | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.2H |  | 3476 | PD-333B
02-VCTP200 | UNIT 2 WATER WASH TANK INLET ISOLATION | 02-10"-CTP0201-1ADA2U | 10" | Gate valve | CTP | 1ADA2U | Water | CL150 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 |  | 3477 | PD-332
02-VCTP219 | INSTRUMENT ISOLATION | 02-0.75"-CTP1023-1BCA2A | 0.75" | Globe valve | CTP | 1BCA2A | Water | CL800 | SWE | SWE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.2H |  | 3478 | PD-332
02-VCTP221 | UNIT 2 ON LINE WASH SUPPLY ISOLATION AT CT PACKAGE | 02-2"-CTP1023-1BCA2A | 2" | Ball valve | CTP | 1BCA2A | Water | CL600 | SWE | SWE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.1 |  | 3479 | PD-332
02-VCTP223 | UNIT 2 ON LINE WASH CLEANING 3 WAY VALVE | 02-2"-CTP1023-1BCA2A | 2" | 3-way valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.1 | T-Port Ball Valve | 3480 | PD-332
02-VCTP225 | UNIT 2 ON LINE WASH SUPPLY ISOLATION AT WW SKID | 02-2"-CTP1025-1BCA2A | 2" | Ball valve | CTP | 1BCA2A | Water | CL600 | SWE | SWE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.1 |  | 3481 | PD-332
02-VCTP229 | INSTRUMENT ISOLATION | 02-0.75"-CTP1033-1BCA2A | 0.75" | Globe valve | CTP | 1BCA2A | Water | CL800 | SWE | SWE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.2H |  | 3482 | PD-332
02-VCTP231 | UNIT 2 OFF LINE WASH SUPPLY ISOLATION AT CT PACKAGE | 02-2"-CTP1033-1BCA2A | 2" | Ball valve | CTP | 1BCA2A | Water | CL600 | SWE | SWE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.1 |  | 3483 | PD-332
02-VCTP233 | UNIT 2 OFF LINE WASH CLEANING 3 WAY VALVE | 02-2"-CTP1033-1BCA2A | 2" | 3-way valve | CTP | 1BCA2A | Water | CL150 | RFFE | RFFE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.1 | T-Port Ball Valve | 3484 | PD-332
02-VCTP235 | UNIT 2 OFF LINE WASH SUPPLY ISOLATION AT WW SKID | 02-2"-CTP1035-1BCA2A | 2" | Ball valve | CTP | 1BCA2A | Water | CL600 | SWE | SWE | 195 | 140 | S-40S |  | No | 94.03.68.150.06.1 |  | 3485 | PD-332
02-VDWS100 | CALCITE FILTER SUPPLY CHECK | 02-3"-DWS1009-1BCA2A | 3" | Check valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S |  | No | 94.03.68.150.03.0 |  | 3486 | PD-333B
02-VDWS101 | INSTRUMENT | 02-0.75"-DWS1001-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 |  | 3487 | PD-333B
02-VDWS104 | UNIT 1 EVAP COOLER SUPPLY ISOLATION | 02-3"-DWS1001-1BCA2A | 3" | Gate valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S |  | No | 94.03.68.150.03.2H |  | 3488 | PD-333B
02-VDWS105 | VENT | 02-0.75"-DWS1015-1BCA2A-1.0 "MOH | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.3H |  | 3489 | PD-050B
02-VDWS106 | CALCITE FILTER ISOLATION | 02-1"-DWS1011-1BCA2A | 1" | Gate valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 |  | 3490 | PD-333B
02-VDWS107 | CALCITE FILTER CO2 INJECTION MODULE ISOLATION | 02-1"-DWS1010-1BCA2A | 1" | Gate valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 |  | 3491 | PD-333B
02-VDWS108 | DRAIN | 02-0.75"-DWS1012-1BCA2A | 0.75" | Gate valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.2H |  | 3492 | PD-333B
02-VDWS109 | INSTRUMENT | 02-0.75"-DWS1013-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.2H |  | 3493 | PD-333B
02-VDWS110 | INSTRUMENT | 02-0.75"-DWS1013-1BCA2A | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.2H |  | 3494 | PD-333B
02-VDWS202 | UNIT 2 SAMPLE PANEL SUPPLY ISOLATION | 02-1"-DWS1004-1BCA2A-1.0 "MOH | 1" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3495 | PD-411
02-VDWS203 | UNIT 2 PHOSPHATE DILUTION SUPPLY ISOLATION | 02-1"-DWS1002-1BCA2A-1.0 "MOH | 1" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3496 | PD-411
02-VDWS204 | VENT | 02-0.75"-DWS1005-1BCA2A | 0.75" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 |  | 3497 | PD-332
02-VDWS205 | WATER WASH SKID ISOLATION | 02-2"-DWS1005-1BCA2A | 2" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S |  | No | 94.03.68.150.06.0 |  | 3498 | PD-332
02-VDWS614 | INSTRUMENT | 02-0.5"-DWS1007-1BCA2A-1.0 "MOH | 0.5" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.2H |  | 3499 | PD-270B
02-VDWS615 | INSTRUMENT | 02-0.5"-DWS1008-1BCA2A-1.0 "MOH | 0.5" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.2H |  | 3500 | PD-270B
02-VDWS616 | CCW HEAD TANK SUPPLY CHECK | 02-2"-DWS1003-1BCA2A-1.0 "MOH | 2" | Check valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3501 | PD-270B
02-VDWS617 | CCW HEAD TANK ISOLATION | 02-2"-DWS1003-1BCA2A-1.0 "MOH | 2" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3502 | PD-270B
02-VDWS620 | VENT | 02-0.75"-DWS1003-1BCA2A-1.0 "MOH | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3503 | PD-270B
02-VDWS636 | CONTROL VALVE ISOLATION | 02-0.75"-DWS1014-1BCA2A-1.0 "MOH | 0.75" | Globe valve | DWS | 1BCA2A | Water | CL800 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.3H |  | 3504 | PD-050B
02-VDWS638 | CONTROL VALVE ISOLATION | 02-4"-DWS1017-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 3505 | PD-050B
02-VDWS639 | CONTROL VALVE ISOLATION | 02-4"-DWS1017-1BCA2A-1.0 "MOH | 4" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 3506 | PD-050B
02-VDWS641 | CONTROL VALVE ISOLATION | 02-6"-DWS1006-1BCA2A-1.0 "MOH | 6" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 3507 | PD-050B
02-VDWS642 | CONTROL VALVE ISOLATION | 02-6"-DWS1006-1BCA2A-1.0 "MOH | 6" | Butterfly valve | DWS | 1BCA2A | Water | CL150 | LUGGED | LUGGED | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.150.04.0 |  | 3508 | PD-050B
02-VDWS643 | DRAIN | 02-0.75"-DWS1006-1BCA2A-1.0 "MOH | 0.75" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3509 | PD-050B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3510 | P&ID
02-VDWS648 | DRAIN | 02-0.75"-DWS1017-1BCA2A-1.0 "MOH | 0.75" | Ball valve | DWS | 1BCA2A | Water | CL600 | SWE | SWE | 170 | 110 | S-40S | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3511 | PD-050B
02-VFGS113 | FLOW METER INLET | 02-10"-FGS1125-1EAL1A-1.0 "MOC | 10" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 302 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 3512 | PD-655B
02-VFGS115 | N2 PURGE ISOLATION | 02-0.75"-FGS1030-1EAL1A-1.0 "EOC | 0.75" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3513 | PD-656B
02-VFGS116 | VENT/DRAIN | 02-0.75"-FGS1125-1EAL1A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 302 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3514 | PD-655B
02-VFGS120 | N2 PURGE ISOLATION | 02-0.75"-FGS1077-1BAA2A-1.0 "AS | 0.75" | Ball valve | FGS | 1BAA2A | Natural Gas | CL600 | SWE | SWE | 75 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3515 | PD-658B
02-VFGS122 | FLOW METER BYPASS | 02-10"-FGS1018-1EAL1A-1.0 "MOC | 10" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 302 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 3516 | PD-655B
02-VFGS123 | EMERGENCY VENT VALVE BYPASS | 02-3"-FGS1035-1EAL1A-1.0 "EOC | 3" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 3517 | PD-656B
02-VFGS124 | TO GT EMERGENCY SHUT OFF VALVE | 02-10"-FGS1125-1EAL1A-1.0 "MOC | 10" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 302 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 3518 | PD-655B
02-VFGS128 | DRAIN | 02-1"-FGS1027-1EAL1A-1.0 "EOC | 1" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3519 | PD-656B
02-VFGS130 | PERFORMANCE HEATER TO EMERGENCY VENT VALVE | 02-3"-FGS1030-1EAL1A-1.0 "EOC | 3" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-40 | 1.0 " | No | 94.03.68.150.07.0 |  | 3520 | PD-656B
02-VFGS134 | PRESSURE REDUCTION UNIT TO CALORIE METER | 02-1"-FGS1025-1EAL1A-1.0 "EOC | 1" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3521 | PD-656B
02-VFGS140 | INSTRUMENTATION ROOT VALVE | 02-0.75"-FGS1040-1EAL1A-1.0 "EOC | 0.75" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3522 | PD-656B
02-VFGS141 | INSTRUMENTATION ROOT VALVE | 02-0.75"-FGS1040-1EAL1A-1.0 "EOC | 0.75" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3523 | PD-656B
02-VFGS143 | N2 PURGE ISOLATION | 02-1"-FGS1074-1EAL1A-1.0 "EOC | 1" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3524 | PD-657B
02-VFGS147 | INSTRUMENTATION ROOT VALVE | 02-1"-FGS1092-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 3525 | PD-657B
02-VFGS148 | INSTRUMENTATION ROOT VALVE | 02-1"-FGS1092-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 3526 | PD-657B
02-VFGS157 | INSTRUMENTATION ROOT VALVE | 02-1"-FGS1092-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 3527 | PD-657B
02-VFGS158 | INSTRUMENT | 02-1"-FGS1092-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 3528 | PD-657B
02-VFGS174 | GAS TURBINE FUEL GAS CARTRIDGE FILTER INLET | 02-12"-FGS1074-1EAL1A-1.5 "EOC | 12" | Ball valve | FGS | 1EAL1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-XS | 1.5 " | No | 94.03.68.150.07.0 |  | 3529 | PD-657B
02-VFGS176 | EQUIPMENT ISOLATION | 02-6"-FGS1076-1EAL2A-1.0 "MOC | 6" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | RFFE | RFFE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3530 | PD-658B
02-VFGS177 | VENT | 02-2"-FGS1078-1ECD1A-1.0 "EOC | 2" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 698 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 3531 | PD-657B
02-VFGS178 | VENT | 02-2"-FGS1078-1ECD1A-1.0 "EOC | 2" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 698 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 3532 | PD-657B
02-VFGS179 | EQUIPMENT ISOLATION | 02-12"-FGS1077-1BAA2A-2.0 "AS | 12" | Ball valve | FGS | 1BAA2A | Natural Gas | CL150 | RFFE | RFFE | 75 | 130 | S-STD | 2.0 " | No | 94.03.68.150.07.0 |  | 3533 | PD-658B
02-VFGS184 | VENT | 02-2"-FGS1080-1ECD1A-1.0 "EOC | 2" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 698 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 3534 | PD-657B
02-VFGS192 | FUEL GAS PURGE CREDIT SHUT OFF VALVE A | 02-12"-FGS1092-1ECD1A-1.5 "EOC | 12" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | RFFE | RFFE | 827 | 608 | S-80S | 1.5 " | No | 94.03.68.150.07.0 |  | 3535 | PD-657B
02-VFGS193 | VENT | 02-1"-FGS1094-1ECD1A-1.0 "EOC | 1" | Ball valve | FGS | 1ECD1A | Natural Gas | CL600 | SWE | SWE | 827 | 608 | S-40S | 1.0 " | No | 94.03.68.150.07.0 |  | 3536 | PD-657B
02-VFGS217 | N2 PURGE ISOLATION | 02-0.75"-FGS1076-1EAL2A-1.0 "MOC | 0.75" | Ball valve | FGS | 1EAL2A | Natural Gas | CL600 | SWE | SWE | 1400 | 130 | S-80 | 1.0 " | No | 94.03.68.150.07.0 |  | 3537 | PD-658B
02-VHPS100 | PIT ROOT VALVE | 02-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 3538 | PD-021B
02-VHPS101 | PIT ROOT VALVE | 02-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 3539 | PD-021B
02-VHPS102 | PIT ROOT VALVE | 02-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 3540 | PD-021B
02-VHPS103 | PIT ROOT VALVE | 02-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 3541 | PD-021B
02-VHPS106 | PTC ROOT VALVE | 02-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 3542 | PD-021B
02-VHPS107 | PTC ROOT VALVE | 02-0.75"-HPS1018-1HBD2A-3.0 "EIC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 3.0 " | No | 94.03.68.150.02.0H | - | 3543 | PD-021B
02-VHPS108 | DRIP LEG DRAIN | 02-2"-HPS1015-1HBD2A-4.0 "EIC | 2" | Ball valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 4.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 3544 | PD-021B
02-VHPS109 | DRIP LEG DRAIN VALVE | 02-2"-HPS1003-1HBD2A-4.0 "EIC | 2" | Gate valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 4.0 " | No | 94.03.68.150.02.0H | FULL BORE | 3545 | PD-021B
02-VHPS110 | DRIP LEG DRAIN VALVE | 02-2"-HPS1003-1HBD2A-4.0 "EIC | 2" | Gate valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 4.0 " | No | 94.03.68.150.02.0H | FULL BORE | 3546 | PD-021B
02-VHPS111 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3547 | PD-020B
02-VHPS112 | PTC ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3548 | PD-020B
02-VHPS113 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3549 | PD-020B
02-VHPS114 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3550 | PD-020B
02-VHPS115 | PTC ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3551 | PD-020B
02-VHPS116 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3552 | PD-020B
02-VHPS119 | PIT ROOT VALVE | 02-0.75"-HPS1151-1EBA1A-1.5 "EOC | 0.75" | Globe valve | HPS | 1EBA1A | Steam | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3553 | PD-020B
02-VHPS120 | PIT ROOT VALVE | 02-0.75"-HPS1151-1EBA1A-1.5 "EOC | 0.75" | Globe valve | HPS | 1EBA1A | Steam | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3554 | PD-020B
02-VHPS121 | PIT ROOT VALVE | 02-0.75"-HPS1151-1EBA1A-1.5 "EOC | 0.75" | Globe valve | HPS | 1EBA1A | Steam | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3555 | PD-020B
02-VHPS122 | PIT ROOT VALVE | 02-0.75"-HPS1151-1EBA1A-1.5 "EOC | 0.75" | Globe valve | HPS | 1EBA1A | Steam | CL1500 | SWE | SWE | 630 | 780 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3556 | PD-020B
02-VHPS123 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3557 | PD-020B
02-VHPS124 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3558 | PD-020B
02-VHPS125 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3559 | PD-020B
02-VHPS126 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3560 | PD-020B
02-VHPS127 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3561 | PD-020B
02-VHPS128 | PIT ROOT VALVE | 02-0.75"-HPS1163-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HPS | 1FBD1A | Steam | CL1500 | SWE | SWE | 630 | 1097 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 3562 | PD-020B
02-VHPS129 | PIT ROOT VALVE | 02-0.75"-HPS1163-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HPS | 1FBD1A | Steam | CL1500 | SWE | SWE | 630 | 1097 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 3563 | PD-020B
02-VHPS130 | PIT ROOT VALVE | 02-0.75"-HPS1010-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3564 | PD-020B
02-VHPS137 | VENT VALVE | 02-0.75"-HPS1174-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3565 | PD-020B
02-VHPS138 | VENT VALVE | 02-0.75"-HPS1174-1HBD2A-2.5 "EOC | 0.75" | Globe valve | HPS | 1HBD2A | Steam | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-160 | 2.5 " | No | 94.03.68.150.02.0H | - | 3566 | PD-020B
02-VHRH100 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3567 | PD-034B
02-VHRH101 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 3568 | PD-034B
02-VHRH102 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3569 | PD-034B
02-VHRH103 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3570 | PD-034B
02-VHRH104 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3571 | PD-034B
02-VHRH105 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1114-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.3H |  | 3572 | PD-034B
02-VHRH106 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3573 | PD-034B
02-VHRH107 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 3574 | PD-034B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3575 | P&ID
02-VHRH108 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3576 | PD-035B
02-VHRH109 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3577 | PD-035B
02-VHRH110 | DRIP LEG DRAIN - AUTOMATED | 02-2"-HRH1112-1FBD1A-4.0 "EIC | 2" | Ball valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13 | 3578 | PD-034B
02-VHRH111 | 01-IKS-HRH100F ISOLATION VALVE | 02-0.75"-HRH1114-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.3H |  | 3579 | PD-034B
02-VHRH113 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1114-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3580 | PD-034B
02-VHRH114 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1114-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3581 | PD-034B
02-VHRH115 | WARMING LINE ISOLATION | 02-2"-HRH1114-1FBD1A-4.0 "EIC | 2" | Gate valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.02.0H | - | 3582 | PD-034B
02-VHRH116 | WARMING LINE ISOLATION | 02-2"-HRH1114-1FBD1A-4.0 "EIC | 2" | Gate valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.02.0H | - | 3583 | PD-034B
02-VHRH120 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-2"-HRH1111-1FBD1A-4.0 "EIC | 2" | Gate valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.02.0H | VALVE TO BE FULL PORT (I.E. 100% BORE AREA) | 3584 | PD-034B
02-VHRH121 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1410-1FBD1A-3.0 "EIC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 3.0 " | No | 94.03.68.150.02.0H | - | 3585 | PD-034B
02-VHRH125 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1121-1EBD1A-2.5 "EOH | 0.75" | Globe valve | HRH | 1EBD1A | Steam | CL800 | SWE | SWE | 150 | 1096 | S-80 | 2.5 " | Yes | 94.03.68.150.02.0H | - | 3586 | PD-034B
02-VHRH126 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1121-1EBD1A-2.5 "EOH | 0.75" | Globe valve | HRH | 1EBD1A | Steam | CL800 | SWE | SWE | 150 | 1096 | S-80 | 2.5 " | Yes | 94.03.68.150.02.0H | - | 3587 | PD-034B
02-VHRH135 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 3588 | PD-034B
02-VHRH136 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 3589 | PD-034B
02-VHRH137 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-2"-HRH1111-1FBD1A-4.0 "EIC | 2" | Gate valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 4.0 " | No | 94.03.68.150.02.0H | VALVE TO BE FULL PORT (I.E. 100% BORE AREA) | 3590 | PD-034B
02-VHRH187 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 3591 | PD-034B
02-VHRH188 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-HRH1250-1FBD1A-2.5 "EOC | 0.75" | Globe valve | HRH | 1FBD1A | Steam | CL1500 | SWE | SWE | 586 | 1096 | S-80 | 2.5 " | No | 94.03.68.150.02.0H | - | 3592 | PD-034B
02-VINA100 | END USER ISOLATION | 02-1"-INA1101-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3593 | PD-562
02-VINA101 | STUB-UP ISOLATION | 02-1"-INA1029-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3594 | PD-555
02-VINA102 | END USER ISOLATION | 02-0.75"-INA1090-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3595 | PD-562
02-VINA103 | STUB-UP ISOLATION | 02-1"-INA1025-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3596 | PD-555
02-VINA104 | STUB-UP ISOLATION | 02-1"-INA1015-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3597 | PD-553
02-VINA105 | DRAIN | 02-0.75"-INA1039-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3598 | PD-559
02-VINA106 | DRAIN | 02-0.75"-INA1501-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3599 | PD-562
02-VINA107 | DRAIN | 02-0.75"-INA1096-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3600 | PD-554
02-VINA108 | END USER ISOLATION | 02-0.75"-INA1329-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3601 | PD-558
02-VINA109 | END USER ISOLATION | 02-0.75"-INA1327-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3602 | PD-558
02-VINA110 | STUB-UP ISOLATION | 02-0.75"-INA1032-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3603 | PD-556
02-VINA111 | END USER ISOLATION | 02-0.75"-INA1330-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3604 | PD-558
02-VINA112 | END USER ISOLATION | 02-0.75"-INA1054-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3605 | PD-562
02-VINA113 | END USER ISOLATION | 02-0.75"-INA1313-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3606 | PD-558
02-VINA114 | END USER ISOLATION | 02-0.75"-INA1038-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3607 | PD-562
02-VINA115 | STUB-UP ISOLATION | 02-1.5"-INA1031-1KFD1A | 1.5" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3608 | PD-554
02-VINA116 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1055-1DCD1A-1.0 "EOI | 0.75" | Globe valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 3609 | PD-562
02-VINA117 | END USER ISOLATION | 02-0.75"-INA1328-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3610 | PD-558
02-VINA118 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1055-1DCD1A-1.0 "EOI | 0.75" | Y stop check valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 3611 | PD-562
02-VINA119 | END USER ISOLATION | 02-0.75"-INA1127-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3612 | PD-562
02-VINA120 | END USER ISOLATION | 02-0.75"-INA1334-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3613 | PD-558
02-VINA121 | END USER ISOLATION | 02-0.75"-INA1333-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3614 | PD-558
02-VINA122 | STUB-UP ISOLATION | 02-0.75"-INA1006-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3615 | PD-556
02-VINA123 | END USER ISOLATION | 02-1"-INA1575-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3616 | PD-553
02-VINA124 | STUB-UP ISOLATION | 02-1"-INA1042-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3617 | PD-562
02-VINA125 | END USER ISOLATION | 02-0.75"-INA1325-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3618 | PD-558
02-VINA126 | STUB-UP ISOLATION | 02-1"-INA1101-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3619 | PD-562
02-VINA127 | END USER ISOLATION | 02-0.75"-INA1314-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3620 | PD-558
02-VINA128 | STUB-UP ISOLATION | 02-1"-INA1092-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3621 | PD-562
02-VINA129 | END USER ISOLATION | 02-0.75"-INA1250-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3622 | PD-558
02-VINA130 | STUB-UP ISOLATION | 02-1"-INA1033-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3623 | PD-562
02-VINA131 | END USER ISOLATION | 02-0.75"-INA1691-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3624 | PD-555
02-VINA132 | END USER ISOLATION | 02-0.75"-INA1072-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3625 | PD-555
02-VINA133 | END USER ISOLATION | 02-0.75"-INA1335-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3626 | PD-558
02-VINA134 | END USER ISOLATION | 02-0.75"-INA1679-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3627 | PD-555
02-VINA135 | END USER ISOLATION | 02-0.75"-INA1474-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3628 | PD-561
02-VINA136 | END USER ISOLATION | 02-0.75"-INA1379-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3629 | PD-559
02-VINA137 | END USER ISOLATION | 02-0.75"-INA1075-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3630 | PD-555
02-VINA138 | END USER ISOLATION | 02-0.75"-INA1076-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3631 | PD-555
02-VINA139 | END USER ISOLATION | 02-2"-INA1019-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3632 | PD-561
02-VINA140 | END USER ISOLATION | 02-0.75"-INA1052-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3633 | PD-562
02-VINA141 | STUB-UP ISOLATION | 02-1"-INA1116-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3634 | PD-562
02-VINA142 | END USER ISOLATION | 02-1"-INA1501-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3635 | PD-562
02-VINA143 | END USER ISOLATION | 02-0.75"-INA1383-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3636 | PD-561
02-VINA144 | STUB-UP ISOLATION | 02-1"-INA1686-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3637 | PD-554
02-VINA145 | END USER ISOLATION | 02-0.75"-INA1385-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3638 | PD-561
02-VINA146 | END USER ISOLATION | 02-0.75"-INA1039-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3639 | PD-559
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3640 | P&ID
02-VINA147 | END USER ISOLATION | 02-0.75"-INA1386-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3641 | PD-561
02-VINA148 | END USER ISOLATION | 02-0.75"-INA1387-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3642 | PD-561
02-VINA149 | END USER ISOLATION | 02-0.75"-INA1249-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3643 | PD-562
02-VINA150 | STUB-UP ISOLATION | 02-1"-INA1121-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3644 | PD-562
02-VINA151 | DRAIN | 02-0.75"-INA1399-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3645 | PD-558
02-VINA152 | END USER ISOLATION | 02-0.75"-INA1689-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3646 | PD-558
02-VINA153 | END USER ISOLATION | 02-0.75"-INA1460-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3647 | PD-561
02-VINA154 | STUB-UP ISOLATION | 02-2"-INA1082-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3648 | PD-556
02-VINA155 | DRAIN | 02-0.75"-INA1018-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3649 | PD-561
02-VINA156 | STUB-UP ISOLATION | 02-2"-INA1086-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3650 | PD-556
02-VINA157 | END USER ISOLATION | 02-0.75"-INA1456-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3651 | PD-558
02-VINA158 | STUB-UP ISOLATION | 02-2"-INA1091-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3652 | PD-562
02-VINA159 | END USER ISOLATION | 02-0.75"-INA1454-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3653 | PD-561
02-VINA160 | END USER ISOLATION | 02-0.75"-INA1469-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3654 | PD-561
02-VINA161 | END USER ISOLATION | 02-0.75"-INA1470-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3655 | PD-561
02-VINA162 | END USER ISOLATION | 02-0.75"-INA1471-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3656 | PD-561
02-VINA163 | END USER ISOLATION | 02-0.75"-INA1472-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3657 | PD-561
02-VINA164 | DRAIN | 02-0.75"-INA1473-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3658 | PD-558
02-VINA165 | END USER ISOLATION | 02-0.75"-INA1040-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3659 | PD-561
02-VINA166 | END USER ISOLATION | 02-0.75"-INA1248-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3660 | PD-562
02-VINA167 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1055-1DCD1A-1.0 "EOI | 0.75" | Check valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 3661 | PD-562
02-VINA168 | END USER ISOLATION | 02-0.75"-INA1447-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3662 | PD-558
02-VINA169 | END USER ISOLATION | 02-0.75"-INA1041-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3663 | PD-562
02-VINA170 | END USER ISOLATION | 02-0.75"-INA1479-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3664 | PD-558
02-VINA171 | END USER ISOLATION | 02-0.75"-INA1046-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3665 | PD-562
02-VINA172 | END USER ISOLATION | 02-0.75"-INA1481-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3666 | PD-561
02-VINA173 | DRAIN | 02-0.75"-INA1398-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3667 | PD-561
02-VINA174 | END USER ISOLATION | 02-0.75"-INA1483-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3668 | PD-559
02-VINA175 | END USER ISOLATION | 02-0.75"-INA1377-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3669 | PD-559
02-VINA176 | END USER ISOLATION | 02-0.75"-INA1378-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3670 | PD-559
02-VINA177 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1050-1DCD1A-1.0 "EOI | 0.75" | Globe valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 3671 | PD-562
02-VINA178 | END USER ISOLATION | 02-0.75"-INA1380-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3672 | PD-561
02-VINA179 | DRAIN | 02-0.75"-INA1090-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3673 | PD-562
02-VINA180 | DRAIN | 02-0.75"-INA1064-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3674 | PD-562
02-VINA181 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1050-1DCD1A-1.0 "EOI | 0.75" | Y stop check valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 3675 | PD-562
02-VINA182 | END USER ISOLATION | 02-0.75"-INA1384-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3676 | PD-561
02-VINA183 | STUB-UP ISOLATION | 02-1"-INA1068-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3677 | PD-562
02-VINA184 | STUB-UP ISOLATION | 02-1"-INA1461-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3678 | PD-554
02-VINA185 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1050-1DCD1A-1.0 "EOI | 0.75" | Check valve | INA | 1DCD1A | AIR | CL800 | SWE | SWE | 406 | 392 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 3679 | PD-562
02-VINA186 | STUB-UP ISOLATION | 02-1"-INA1094-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3680 | PD-554
02-VINA187 | DRAIN | 02-0.75"-INA1686-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3681 | PD-554
02-VINA188 | END USER ISOLATION | 02-0.75"-INA1141-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3682 | PD-561
02-VINA189 | DRAIN | 02-0.75"-INA1010-1KFB1A | 0.75" | Ball valve | INA | 1KFB1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3683 | PD-554
02-VINA190 | STUB-UP ISOLATION | 02-2"-INA1018-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3684 | PD-555
02-VINA191 | DRAIN | 02-0.75"-INA1076-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3685 | PD-558
02-VINA192 | DRAIN | 02-0.75"-INA1034-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3686 | PD-562
02-VINA193 | STUB-UP ISOLATION | 02-1"-INA1045-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3687 | PD-554
02-VINA194 | DRAIN | 02-0.75"-INA1454-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3688 | PD-561
02-VINA195 | STUB-UP ISOLATION | 02-2"-INA1016-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3689 | PD-554
02-VINA196 | STUB-UP ISOLATION | 02-0.75"-INA1022-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3690 | PD-554
02-VINA197 | END USER ISOLATION | 02-0.75"-INA1398-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3691 | PD-561
02-VINA198 | DRAIN | 02-0.75"-INA1461-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3692 | PD-554
02-VINA199 | STUB-UP ISOLATION | 02-1"-INA1028-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3693 | PD-555
02-VINA200 | END USER ISOLATION | 02-0.75"-INA1401-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3694 | PD-558
02-VINA201 | END USER ISOLATION | 02-0.75"-INA1402-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3695 | PD-558
02-VINA202 | DRAIN | 02-0.75"-INA1454-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3696 | PD-561
02-VINA203 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1076-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3697 | PD-554
02-VINA204 | DRAIN | 02-0.75"-INA1249-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3698 | PD-562
02-VINA205 | END USER ISOLATION | 02-0.75"-INA1406-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3699 | PD-561
02-VINA206 | END USER ISOLATION | 02-1.5"-INA1400-1KFD1A | 1.5" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3700 | PD-558
02-VINA207 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-0.75"-INA1399-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3701 | PD-558
02-VINA208 | END USER ISOLATION | 02-0.75"-INA1409-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3702 | PD-561
02-VINA209 | END USER ISOLATION | 02-0.75"-INA1408-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3703 | PD-561
02-VINA210 | END USER ISOLATION | 02-0.75"-INA1411-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3704 | PD-561
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3705 | P&ID
02-VINA211 | END USER ISOLATION | 02-0.75"-INA1093-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3706 | PD-561
02-VINA212 | END USER ISOLATION | 02-0.75"-INA1312-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3707 | PD-558
02-VINA213 | STUB-UP ISOLATION | 02-1"-INA1026-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3708 | PD-555
02-VINA214 | STUB-UP ISOLATION | 02-0.75"-INA1659-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3709 | PD-554
02-VINA215 | END USER ISOLATION | 02-0.75"-INA1004-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3710 | PD-561
02-VINA216 | END USER ISOLATION | 02-0.75"-INA1447-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3711 | PD-558
02-VINA217 | DRAIN | 02-0.75"-INA1460-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3712 | PD-561
02-VINA218 | STUB-UP ISOLATION | 02-1"-INA1076-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3713 | PD-554
02-VINA219 | END USER ISOLATION | 02-0.75"-INA1140-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3714 | PD-561
02-VINA220 | DRAIN | 02-0.75"-INA1011-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3715 | PD-561
02-VINA221 | STUB-UP ISOLATION | 02-2"-INA1023-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3716 | PD-555
02-VINA222 | END USER ISOLATION | 02-2"-INA1098-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3717 | PD-554
02-VINA223 | END USER ISOLATION | 02-1.5"-INA1096-1KFD1A | 1.5" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3718 | PD-554
02-VINA224 | STUB-UP ISOLATION | 02-1"-INA1027-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3719 | PD-555
02-VINA225 | DRAIN | 02-0.75"-INA1140-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3720 | PD-561
02-VINA226 | END USER ISOLATION | 02-0.75"-INA1242-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3721 | PD-561
02-VINA227 | END USER ISOLATION | 02-0.75"-INA1003-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3722 | PD-561
02-VINA228 | END USER ISOLATION | 02-0.75"-INA1410-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3723 | PD-561
02-VINA229 | END USER ISOLATION | 02-0.75"-INA1407-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3724 | PD-561
02-VINA230 | END USER ISOLATION | 02-0.75"-INA1405-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3725 | PD-558
02-VINA231 | DRAIN | 02-0.75"-INA1140-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3726 | PD-561
02-VINA232 | END USER ISOLATION | 02-0.75"-INA1403-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3727 | PD-558
02-VINA233 | END USER ISOLATION | 02-0.75"-INA1375-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3728 | PD-558
02-VINA234 | DRAIN | 02-0.75"-INA1068-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3729 | PD-562
02-VINA235 | END USER ISOLATION | 02-0.75"-INA1315-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3730 | PD-558
02-VINA236 | END USER ISOLATION | 02-0.75"-INA1331-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3731 | PD-558
02-VINA237 | END USER ISOLATION | 02-0.75"-INA1332-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3732 | PD-558
02-VINA238 | END USER ISOLATION | 02-0.75"-INA1353-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3733 | PD-561
02-VINA239 | END USER ISOLATION | 02-0.75"-INA1001-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3734 | PD-558
02-VINA240 | END USER ISOLATION | 02-0.75"-INA1351-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3735 | PD-560
02-VINA241 | END USER ISOLATION | 02-0.75"-INA1340-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3736 | PD-560
02-VINA242 | END USER ISOLATION | 02-0.75"-INA1349-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3737 | PD-560
02-VINA243 | END USER ISOLATION | 02-0.75"-INA1348-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3738 | PD-561
02-VINA244 | END USER ISOLATION | 02-0.75"-INA1347-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3739 | PD-561
02-VINA245 | END USER ISOLATION | 02-1"-INA1688-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3740 | PD-561
02-VINA246 | END USER ISOLATION | 02-0.75"-INA1345-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3741 | PD-560
02-VINA248 | END USER ISOLATION | 02-0.75"-INA1659-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3742 | PD-554
02-VINA251 | END USER ISOLATION | 02-0.75"-INA1010-1KFB1A | 0.75" | Ball valve | INA | 1KFB1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3743 | PD-554
02-VINA254 | END USER ISOLATION | 02-0.75"-INA1011-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3744 | PD-561
02-VINA258 | DRAIN | 02-0.75"-INA1068-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3745 | PD-562
02-VINA259 | END USER ISOLATION | 02-0.75"-INA1002-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3746 | PD-562
02-VINA260 | END USER ISOLATION | 02-0.75"-INA1020-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3747 | PD-562
02-VINA261 | END USER ISOLATION | 02-0.75"-INA1021-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3748 | PD-562
02-VINA262 | END USER ISOLATION | 02-0.75"-INA1024-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3749 | PD-562
02-VINA263 | DRAIN | 02-0.75"-INA1032-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3750 | PD-562
02-VINA264 | END USER ISOLATION | 02-0.75"-INA1034-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3751 | PD-562
02-VINA266 | DRAIN | 02-0.75"-INA1471-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3752 | PD-561
02-VINA267 | END USER ISOLATION | 02-0.75"-INA1035-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3753 | PD-562
02-VINA268 | END USER ISOLATION | 02-0.75"-INA1036-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3754 | PD-562
02-VINA269 | DRAIN | 02-0.75"-INA1469-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3755 | PD-561
02-VINA270 | DRAIN | 02-0.75"-INA1476-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3756 | PD-561
02-VINA271 | DRAIN | 02-0.75"-INA1476-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3757 | PD-561
02-VINA272 | END USER ISOLATION | 02-1"-INA1311-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3758 | PD-561
02-VINA273 | END USER ISOLATION | 02-0.75"-INA1104-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3759 | PD-562
02-VINA274 | END USER ISOLATION | 02-0.75"-INA1102-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3760 | PD-562
02-VINA275 | DRAIN | 02-0.75"-INA1236-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3761 | PD-559
02-VINA276 | END USER ISOLATION | 02-0.75"-INA1236-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3762 | PD-559
02-VINA277 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-1"-INA1109-1ECD1A-1.0 "EOI | 1" | Y stop check valve | INA | 1ECD1A | AIR | CL800 | SWE | SWE | 682 | 482 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 3763 | PD-562
02-VINA278 | AIR SUPPLY OVERPRESSURE PROTECTION | 02-1"-INA1109-1ECD1A-1.0 "EOI | 1" | Check valve | INA | 1ECD1A | AIR | CL800 | SWE | SWE | 682 | 482 | S-40S | 1.0 " | No | 94.03.68.150.06.4 |  | 3764 | PD-562
02-VINA280 | END USER ISOLATION | 02-0.75"-INA1105-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3765 | PD-562
02-VINA281 | DRAIN | 02-0.75"-INA1659-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3766 | PD-554
02-VINA282 | DRAIN | 02-0.75"-INA1072-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3767 | PD-555
02-VINA283 | DRAIN | 02-0.75"-INA1030-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3768 | PD-555
02-VINA284 | DRAIN | 02-0.75"-INA1029-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3769 | PD-555
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3770 | P&ID
02-VINA285 | DRAIN | 02-0.75"-INA1680-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3771 | PD-555
02-VINA286 | DRAIN | 02-0.75"-INA1028-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3772 | PD-555
02-VINA287 | END USER ISOLATION | 02-0.75"-INA1234-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3773 | PD-558
02-VINA288 | DRAIN | 02-0.75"-INA1076-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3774 | PD-555
02-VINA289 | END USER ISOLATION | 02-0.75"-INA1027-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3775 | PD-555
02-VINA290 | DRAIN | 02-0.75"-INA1037-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3776 | PD-555
02-VINA291 | DRAIN | 02-0.75"-INA1026-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3777 | PD-555
02-VINA292 | DRAIN | 02-0.75"-INA1080-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3778 | PD-555
02-VINA294 | DRAIN | 02-0.75"-INA1230-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3779 | PD-562
02-VINA295 | DRAIN | 02-0.75"-INA1086-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3780 | PD-556
02-VINA296 | END USER ISOLATION | 02-0.75"-INA1224-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3781 | PD-562
02-VINA298 | DRAIN | 02-0.75"-INA1002-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3782 | PD-562
02-VINA299 | DRAIN | 02-0.75"-INA1020-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3783 | PD-562
02-VINA300 | END USER ISOLATION | 02-0.75"-INA1344-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3784 | PD-560
02-VINA301 | END USER ISOLATION | 02-0.75"-INA1355-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3785 | PD-560
02-VINA302 | END USER ISOLATION | 02-0.75"-INA1336-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3786 | PD-560
02-VINA303 | END USER ISOLATION | 02-0.75"-INA1350-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3787 | PD-560
02-VINA304 | END USER ISOLATION | 02-0.75"-INA1000-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3788 | PD-560
02-VINA305 | END USER ISOLATION | 02-0.75"-INA1352-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3789 | PD-560
02-VINA307 | END USER ISOLATION | 02-0.75"-INA1337-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3790 | PD-560
02-VINA308 | END USER ISOLATION | 02-0.75"-INA1343-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3791 | PD-560
02-VINA309 | END USER ISOLATION | 02-0.75"-INA1338-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3792 | PD-560
02-VINA310 | DRAIN | 02-0.75"-INA1021-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3793 | PD-562
02-VINA311 | END USER ISOLATION | 02-0.75"-INA1342-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3794 | PD-560
02-VINA312 | END USER ISOLATION | 02-0.75"-INA1354-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3795 | PD-560
02-VINA313 | END USER ISOLATION | 02-0.75"-INA1339-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3796 | PD-560
02-VINA314 | END USER ISOLATION | 02-0.75"-INA1232-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3797 | PD-559
02-VINA315 | DRAIN | 02-0.75"-INA1232-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3798 | PD-559
02-VINA316 | END USER ISOLATION | 02-0.75"-INA1229-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3799 | PD-559
02-VINA317 | DRAIN | 02-0.75"-INA1024-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3800 | PD-562
02-VINA318 | DRAIN | 02-0.75"-INA1038-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3801 | PD-562
02-VINA319 | END USER ISOLATION | 02-0.75"-INA1227-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3802 | PD-559
02-VINA320 | DRAIN | 02-0.75"-INA1226-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3803 | PD-562
02-VINA321 | DRAIN | 02-0.75"-INA1127-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3804 | PD-562
02-VINA322 | DRAIN | 02-0.75"-INA1476-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3805 | PD-561
02-VINA323 | END USER ISOLATION | 02-0.75"-INA1220-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3806 | PD-559
02-VINA324 | DRAIN | 02-0.75"-INA1478-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3807 | PD-561
02-VINA325 | END USER ISOLATION | 02-0.75"-INA1219-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3808 | PD-559
02-VINA326 | DRAIN | 02-0.75"-INA1478-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3809 | PD-561
02-VINA327 | DRAIN | 02-0.75"-INA1470-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3810 | PD-561
02-VINA328 | DRAIN | 02-0.75"-INA1481-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3811 | PD-561
02-VINA329 | DRAIN | 02-0.75"-INA1481-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3812 | PD-561
02-VINA330 | DRAIN | 02-0.75"-INA1304-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3813 | PD-561
02-VINA331 | DRAIN | 02-0.75"-INA1348-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3814 | PD-561
02-VINA332 | END USER ISOLATION | 02-1"-INA1278-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3815 | PD-561
02-VINA333 | DRAIN | 02-0.75"-INA1311-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3816 | PD-561
02-VINA334 | END USER ISOLATION | 02-1"-INA1153-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3817 | PD-561
02-VINA335 | DRAIN | 02-0.75"-INA1278-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3818 | PD-561
02-VINA336 | DRAIN | 02-0.75"-INA1311-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3819 | PD-561
02-VINA337 | END USER ISOLATION | 02-0.75"-INA1276-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3820 | PD-560
02-VINA338 | DRAIN | 02-0.75"-INA1347-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3821 | PD-561
02-VINA339 | DRAIN | 02-0.75"-INA1278-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3822 | PD-561
02-VINA340 | END USER ISOLATION | 02-0.75"-INA1275-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3823 | PD-560
02-VINA341 | DRAIN | 02-0.75"-INA1353-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3824 | PD-561
02-VINA342 | DRAIN | 02-0.75"-INA1153-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3825 | PD-561
02-VINA343 | END USER ISOLATION | 02-0.75"-INA1244-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3826 | PD-561
02-VINA344 | DRAIN | 02-0.75"-INA1688-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3827 | PD-561
02-VINA345 | END USER ISOLATION | 02-1"-INA1150-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3828 | PD-561
02-VINA346 | END USER ISOLATION | 02-0.75"-INA1396-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3829 | PD-561
02-VINA347 | END USER ISOLATION | 02-0.75"-INA1397-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3830 | PD-561
02-VINA348 | END USER ISOLATION | 02-0.75"-INA1687-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3831 | PD-561
02-VINA349 | END USER ISOLATION | 02-0.75"-INA1478-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3832 | PD-561
02-VINA350 | END USER ISOLATION | 02-0.75"-INA1480-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3833 | PD-561
02-VINA351 | END USER ISOLATION | 02-0.75"-INA1476-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3834 | PD-561
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3835 | P&ID
02-VINA352 | DRAIN | 02-0.75"-INA1150-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3836 | PD-561
02-VINA353 | DRAIN | 02-0.75"-INA1219-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3837 | PD-559
02-VINA354 | DRAIN | 02-0.75"-INA1220-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3838 | PD-559
02-VINA355 | DRAIN | 02-0.75"-INA1220-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3839 | PD-559
02-VINA356 | DRAIN | 02-0.75"-INA1277-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3840 | PD-561
02-VINA357 | DRAIN | 02-0.75"-INA1040-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3841 | PD-561
02-VINA358 | DRAIN | 02-0.75"-INA1040-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3842 | PD-561
02-VINA359 | DRAIN | 02-0.75"-INA1277-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3843 | PD-561
02-VINA360 | DRAIN | 02-0.75"-INA1277-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3844 | PD-561
02-VINA361 | DRAIN | 02-0.75"-INA1277-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3845 | PD-561
02-VINA362 | DRAIN | 02-0.75"-INA1396-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3846 | PD-561
02-VINA363 | DRAIN | 02-0.75"-INA1397-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3847 | PD-561
02-VINA364 | DRAIN | 02-0.75"-INA1490-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3848 | PD-561
02-VINA365 | DRAIN | 02-0.75"-INA1249-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3849 | PD-562
02-VINA366 | DRAIN | 02-0.75"-INA1248-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3850 | PD-562
02-VINA367 | END USER ISOLATION | 02-0.75"-INA1057-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3851 | PD-558
02-VINA368 | END USER ISOLATION | 02-0.75"-INA1247-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3852 | PD-562
02-VINA369 | END USER ISOLATION | 02-0.75"-INA1058-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3853 | PD-558
02-VINA370 | END USER ISOLATION | 02-0.75"-INA1114-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3854 | PD-562
02-VINA371 | DRAIN | 02-0.75"-INA1058-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3855 | PD-558
02-VINA372 | END USER ISOLATION | 02-0.75"-INA1226-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3856 | PD-562
02-VINA373 | DRAIN | 02-0.75"-INA1480-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3857 | PD-561
02-VINA374 | DRAIN | 02-0.75"-INA1456-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3858 | PD-558
02-VINA376 | DRAIN | 02-0.75"-INA1234-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3859 | PD-558
02-VINA377 | DRAIN | 02-0.75"-INA1479-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3860 | PD-558
02-VINA379 | END USER ISOLATION | 02-1"-INA1304-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3861 | PD-561
02-VINA381 | END USER ISOLATION | 02-0.75"-INA1230-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3862 | PD-562
02-VINA383 | DRAIN | 02-0.75"-INA1057-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3863 | PD-558
02-VINA384 | DRAIN | 02-0.75"-INA1077-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3864 | PD-558
02-VINA385 | DRAIN | 02-0.75"-INA1329-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3865 | PD-558
02-VINA386 | DRAIN | 02-0.75"-INA1327-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3866 | PD-558
02-VINA387 | DRAIN | 02-0.75"-INA1312-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3867 | PD-558
02-VINA388 | DRAIN | 02-0.75"-INA1328-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3868 | PD-558
02-VINA389 | DRAIN | 02-0.75"-INA1313-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3869 | PD-558
02-VINA390 | DRAIN | 02-0.75"-INA1019-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3870 | PD-561
02-VINA391 | DRAIN | 02-0.75"-INA1380-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3871 | PD-561
02-VINA392 | DRAIN | 02-0.75"-INA1380-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3872 | PD-561
02-VINA393 | DRAIN | 02-0.75"-INA1401-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3873 | PD-558
02-VINA394 | DRAIN | 02-0.75"-INA1378-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3874 | PD-559
02-VINA396 | DRAIN | 02-0.75"-INA1377-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3875 | PD-559
02-VINA397 | DRAIN | 02-0.75"-INA1474-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3876 | PD-561
02-VINA399 | DRAIN | 02-0.75"-INA1094-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3877 | PD-561
02-VINA400 | END USER ISOLATION | 02-0.75"-INA1488-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3878 | PD-561
02-VINA401 | END USER ISOLATION | 02-0.75"-INA1489-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3879 | PD-561
02-VINA402 | END USER ISOLATION | 02-0.75"-INA1490-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3880 | PD-561
02-VINA410 | END USER ISOLATION | 02-1"-INA1092-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3881 | PD-562
02-VINA411 | END USER ISOLATION | 02-0.75"-INA1064-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3882 | PD-562
02-VINA412 | END USER ISOLATION | 02-1"-INA1121-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3883 | PD-562
02-VINA413 | END USER ISOLATION | 02-1"-INA1007-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3884 | PD-562
02-VINA414 | END USER ISOLATION | 02-0.75"-INA1008-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3885 | PD-562
02-VINA415 | STUB-UP ISOLATION | 02-1"-INA1007-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3886 | PD-562
02-VINA416 | DRAIN | 02-0.75"-INA1094-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3887 | PD-561
02-VINA417 | STUB-UP ISOLATION | 02-1"-INA1030-1KFD1A | 1" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3888 | PD-555
02-VINA418 | END USER ISOLATION | 02-0.75"-INA1680-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3889 | PD-555
02-VINA419 | END USER ISOLATION | 02-0.75"-INA1066-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3890 | PD-555
02-VINA420 | END USER ISOLATION | 02-0.75"-INA1037-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3891 | PD-555
02-VINA421 | END USER ISOLATION | 02-0.75"-INA1081-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3892 | PD-555
02-VINA422 | END USER ISOLATION | 02-0.75"-INA1080-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3893 | PD-555
02-VINA424 | DRAIN | 02-0.75"-INA1250-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3894 | PD-558
02-VINA425 | DRAIN | 02-0.75"-INA1333-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3895 | PD-558
02-VINA426 | DRAIN | 02-0.75"-INA1334-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3896 | PD-558
02-VINA428 | DRAIN | 02-0.75"-INA1403-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3897 | PD-558
02-VINA429 | END USER ISOLATION | 02-0.75"-INA1516-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3898 | PD-558
02-VINA430 | DRAIN | 02-0.75"-INA1516-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3899 | PD-558
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3900 | P&ID
02-VINA431 | DRAIN | 02-0.75"-INA1405-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3901 | PD-558
02-VINA432 | DRAIN | 02-0.75"-INA1399-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3902 | PD-558
02-VINA433 | DRAIN | 02-0.75"-INA1400-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3903 | PD-558
02-VINA434 | DRAIN | 02-0.75"-INA1399-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3904 | PD-558
02-VINA435 | DRAIN | 02-0.75"-INA1098-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3905 | PD-558
02-VINA436 | DRAIN | 02-0.75"-INA1314-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3906 | PD-558
02-VINA438 | DRAIN | 02-0.75"-INA1315-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3907 | PD-558
02-VINA439 | DRAIN | 02-0.75"-INA1341-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3908 | PD-558
02-VINA440 | DRAIN | 02-0.75"-INA1331-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3909 | PD-558
02-VINA441 | DRAIN | 02-0.75"-INA1332-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3910 | PD-558
02-VINA442 | DRAIN | 02-0.75"-INA1340-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3911 | PD-560
02-VINA443 | DRAIN | 02-0.75"-INA1001-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3912 | PD-558
02-VINA445 | DRAIN | 02-0.75"-INA1351-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3913 | PD-560
02-VINA446 | DRAIN | 02-0.75"-INA1345-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3914 | PD-560
02-VINA447 | DRAIN | 02-0.75"-INA1492-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3915 | PD-558
02-VINA448 | DRAIN | 02-0.75"-INA1350-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3916 | PD-560
02-VINA450 | DRAIN | 02-0.75"-INA1352-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3917 | PD-560
02-VINA451 | DRAIN | 02-0.75"-INA1000-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3918 | PD-560
02-VINA452 | DRAIN | 02-0.75"-INA1336-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3919 | PD-560
02-VINA453 | DRAIN | 02-0.75"-INA1355-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3920 | PD-560
02-VINA454 | DRAIN | 02-0.75"-INA1344-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3921 | PD-560
02-VINA455 | DRAIN | 02-0.75"-INA1343-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3922 | PD-560
02-VINA456 | DRAIN | 02-0.75"-INA1338-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3923 | PD-560
02-VINA457 | DRAIN | 02-0.75"-INA1342-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3924 | PD-560
02-VINA458 | DRAIN | 02-0.75"-INA1354-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3925 | PD-560
02-VINA459 | DRAIN | 02-0.75"-INA1339-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3926 | PD-560
02-VINA460 | END USER ISOLATION | 02-0.75"-INA1341-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3927 | PD-558
02-VINA461 | DRAIN | 02-0.75"-INA1102-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3928 | PD-562
02-VINA462 | END USER ISOLATION | 02-0.75"-INA1115-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3929 | PD-562
02-VINA463 | DRAIN | 02-0.75"-INA1232-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3930 | PD-559
02-VINA464 | STUB-UP ISOLATION | 02-2"-INA1277-1KFD1A | 2" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3931 | PD-556
02-VINA469 | DRAIN | 02-0.75"-INA1349-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3932 | PD-560
02-VINA470 | DRAIN | 02-0.75"-INA1695-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3933 | PD-562
02-VINA475 | DRAIN | 02-0.75"-INA1219-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3934 | PD-556
02-VINA476 | DRAIN | 02-0.75"-INA1219-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3935 | PD-556
02-VINA479 | END USER ISOLATION | 02-0.75"-INA1492-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3936 | PD-558
02-VINA480 | END USER ISOLATION | 02-0.75"-INA1491-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3937 | PD-558
02-VINA500 | DRAIN | 02-0.75"-INA1232-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3938 | PD-559
02-VINA515 | DRAIN | 02-0.75"-INA1229-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3939 | PD-559
02-VINA545 | DRAIN | 02-0.75"-INA1082-1KFD1A | 0.75" | Ball valve | INA | 1KFD1A | AIR | CL125 | P | P | 145 | 140 | Type K |  | No | 94.03.68.150.06.5 |  | 3940 | PD-561
02-VLPS101 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-1"-LPS1408-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3941 | PD-040B
02-VLPS102 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1409-1DAA1A-2.0 "EIC | 0.75" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3942 | PD-040B
02-VLPS103 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-1"-LPS1409-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3943 | PD-040B
02-VLPS104 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-1"-LPS1410-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3944 | PD-040B
02-VLPS106 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-1"-LPS1411-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3945 | PD-040B
02-VLPS107 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1411-1DAA1A-2.0 "EIC | 0.75" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3946 | PD-040B
02-VLPS108 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-2"-LPS1400-1DAA1A-2.0 "EIC | 2" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | VALVE TO BE FULL PORT (I.E. 100% BORE AREA) | 3947 | PD-040B
02-VLPS109 | DRIP LEG DRAIN | 02-2"-LPS1401-1DAA1A-2.0 "EIC | 2" | Ball valve | LPS | 1DAA1A | Steam | CL600 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 3948 | PD-040B
02-VLPS111 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-2"-LPS1400-1DAA1A-2.0 "EIC | 2" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | VALVE TO BE FULL PORT (I.E. 100% BORE AREA) | 3949 | PD-040B
02-VLPS112 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1465-1DAA1A-1.5 "EOC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3950 | PD-040B
02-VLPS123 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1465-1DAA1A-1.5 "EOC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 1.5 " | No | 94.03.68.150.02.0H | - | 3951 | PD-040B
02-VLPS142 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1466-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3952 | PD-040B
02-VLPS147 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1473-1BAA1A-1.5 "EOH | 0.75" | Globe valve | LPS | 1BAA1A | Steam | CL1500 | SWE | SWE | 50 | 624 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3953 | PD-041B
02-VLPS149 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-2"-LPS1413-1DAA1A-2.0 "EIC | 2" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3954 | PD-041B
02-VLPS150 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-2"-LPS1413-1DAA1A-2.0 "EIC | 2" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3955 | PD-041B
02-VLPS151 | DRIP LEG DRAIN | 02-2"-LPS1429-1DAA1A-2.0 "EIC | 2" | Ball valve | LPS | 1DAA1A | Steam | CL600 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.08.0 | MINIMUM ALLOWABLE BORE DIAMETER TO SATIFY TDP-1, SECTION 3.7.13; GEAR OPERATED | 3956 | PD-041B
02-VLPS152 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1463-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3957 | PD-040B
02-VLPS161 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1473-1BAA1A-1.5 "EOH | 0.75" | Globe valve | LPS | 1BAA1A | Steam | CL1500 | SWE | SWE | 50 | 624 | S-80 | 1.5 " | Yes | 94.03.68.150.02.0H | RATED FOR VACUUM SERVICE | 3958 | PD-041B
02-VLPS163 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1466-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3959 | PD-041B
02-VLPS164 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1463-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3960 | PD-040B
02-VLPS167 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1466-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3961 | PD-040B
02-VLPS169 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-1"-LPS1405-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3962 | PD-041B
02-VLPS170 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-1"-LPS1406-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3963 | PD-041B
02-VLPS171 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-1"-LPS1407-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3964 | PD-041B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 3965 | P&ID
02-VLPS172 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-1"-LPS1404-1DAA1A-2.0 "EIC | 1" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3966 | PD-041B
02-VLPS173 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1466-1DAA1A-2.0 "EIC | 0.75" | Globe valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3967 | PD-041B
02-VLPS175 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1405-1DAA1A-2.0 "EIC | 0.75" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3968 | PD-041B
02-VLPS177 | VENT/DRAIN/INSTRUMENTATION ROOT VALVE | 02-0.75"-LPS1407-1DAA1A-2.0 "EIC | 0.75" | Gate valve | LPS | 1DAA1A | Steam | CL800 | SWE | SWE | 119 | 624 | S-80 | 2.0 " | No | 94.03.68.150.02.0H | - | 3969 | PD-041B
02-VPDR200 | TRANSFORMER CONTAINMENT ISOLATION | 02-4"-PDR0243-1ADA2U | 4" | Gate valve | PDR | 1ADA2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 3970 | PD-971
02-VPDR201 | TRANSFORMER CONTAINMENT ISOLATION | 02-4"-PDR0245-1ADA2U | 4" | Gate valve | PDR | 1ADA2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 3971 | PD-971
02-VPDR205 | OWS INLET ISOLATION | 02-12"-PDR0201-1ADA2U | 12" | Gate valve | PDR | 1ADA2U | OIL/WATER | CL125 | FFFE | FFFE | 0 | 125 | S-SV |  | No | 93.70.02 | UNDERGROUND VALVE W/VALVE BOX AND TEE EXTENSION | 3972 | PD-960B
02-VPDR207 | TRENCH DRAIN CHECK/FLAPPER VALVE | 02-12"-PDR0253-1ADA1U | 12" | Check valve | PDR | 1ADA1U | OIL/WATER | CL150 | NONE/INLINE | INTERNAL CLAMP | 0 | 200 | S-SV |  | No | 94.03.56.100.1 | TIDEFLEX CHECKMATE OR EQUIV., RUBBER INLINE CHECK VALVE, PIPE ID: 11.94 +/- 0.19 IN, MATERIALS SUITABLE FOR OILY WATER WORKING FLUID | 3973 | PD-973
02-VPDR208 | TRENCH DRAIN CHECK/FLAPPER VALVE | 02-4"-PDR0257-1ADA1U | 4" | Check valve | PDR | 1ADA1U | OIL/WATER | CL150 | NONE/INLINE | INTERNAL CLAMP | 0 | 200 | S-SV |  | No | 94.03.56.100.1 | TIDEFLEX CHECKMATE OR EQUIV., RUBBER INLINE CHECK VALVE, PIPE ID: 3.94 +/- 0.09 IN, MATERIALS SUITABLE FOR OILY WATER WORKING FLUID | 3974 | PD-973
02-VPDR209 | TRENCH DRAIN CHECK/FLAPPER VALVE | 02-12"-PDR0262-1ADA1U | 12" | Check valve | PDR | 1ADA1U | OIL/WATER | CL150 | NONE/INLINE | INTERNAL CLAMP | 0 | 200 | S-SV |  | No | 94.03.56.100.1 | TIDEFLEX CHECKMATE OR EQUIV., RUBBER INLINE CHECK VALVE, PIPE ID: 11.94 +/- 0.19 IN, MATERIALS SUITABLE FOR OILY WATER WORKING FLUID | 3975 | PD-973
02-VSMP100 | UNIT 2 SAMPLE PANEL HP BLOWDOWN HEADER DRAIN ISOLATION VALVE | 02-0.75"-SMP1011-1DCA3A-2.5 "EOH | 0.75" | Gate valve | SMP | 1DCA3A | Water | CL600 | SWE | SWE | 15 | 1097 | S-40S | 2.5 " | Yes | 94.03.68.150.02.2H |  | 3976 | PD-500B
02-VSTP100 | HP CONTROL VALVE HP STEM LEAK CHECK VALVE | 02-1.5"-STP1060-1GBB1A-3.5 "EIC | 1.5" | Check valve | STP | 1GBB1A | Steam/Water | CL1500 | SWE | SWE | 630 | 1073 | S-160 | 3.5 " | No | 94.03.68.150.06.1H | PISTON LIFT | 3977 | PD-303B
02-VSTP101 | HP STOP VALVE HP STEM LEAK CHECK VALVE | 02-1.5"-STP1041-1GBB1A-3.5 "EIC | 1.5" | Check valve | STP | 1GBB1A | Steam/Water | CL1500 | SWE | SWE | 630 | 1073 | S-160 | 3.5 " | No | 94.03.68.150.02.1H | PISTON LIFT | 3978 | PD-303B
02-VSTP102 | HP STEM LEAK TO CRH CHECK VALVE | 02-2"-STP1041-1GBB1A-4.0 "EIC | 2" | Check valve | STP | 1GBB1A | Steam/Water | CL1500 | SWE | SWE | 630 | 1073 | S-160 | 4.0 " | No | 94.03.68.150.02.1H | PISTON LIFT | 3979 | PD-303B
02-VSTP103 | HP STEM LEAK TO HP DRN TANK CHECK VALVE | 02-2"-STP1043-1GBB1A-4.0 "EIC | 2" | Check valve | STP | 1GBB1A | Steam/Water | CL1500 | SWE | SWE | 630 | 1073 | S-160 | 4.0 " | No | 94.03.68.150.02.1H | PISTON LIFT | 3980 | PD-303B
02-VSTP104 | HP STEAM INLET PIPE DRAIN MANUAL ISOLATION | 02-1.5"-STP1089-1HBD1A-3.5 "EIC | 1.5" | Gate valve | STP | 1HBD1A | Steam/Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 3.5 " | No | 94.03.68.150.02.1H | RATED FOR VACUUM SERVICE | 3981 | PD-303B
02-VSTP105 | CMV SEAT DRAIN MANUAL ISOLATION | 02-1.5"-STP1020-1HBD1A-3.5 "EIC | 1.5" | Gate valve | STP | 1HBD1A | Steam/Water | CL2500 SPL | SWE | SWE | 2534 | 1097 | S-XXS | 3.5 " | No | 94.03.68.150.02.1H |  | 3982 | PD-303B
02-VSTP106 | IP STEAM INLET PIPE DRAIN MANUAL ISOLATION | 02-1"-STP1064-1FBD1A-3.5 "EIC | 1" | Gate valve | STP | 1FBD1A | Steam/Water | CL1500 | SWE | SWE | 624 | 1096 | S-80 | 3.5 " | No | 94.03.68.150.02.1H | RATED FOR VACUUM SERVICE | 3983 | PD-303B
02-VSTP107 | CRV SEAT DRAIN MANUAL ISOLATION | 02-1"-STP1066-1FBD1A-3.5 "EIC | 1" | Gate valve | STP | 1FBD1A | Steam/Water | CL1500 | SWE | SWE | 624 | 1096 | S-80 | 3.5 " | No | 94.03.68.150.02.1H |  | 3984 | PD-303B
02-VSTP108 | LP STEAM STRAINER DRAIN MANUAL ISOLATION | 02-1"-STP1068-1DAA1A-2.0 "EIC | 1" | Gate valve | STP | 1DAA1A | Steam/Water | CL800 | SWE | SWE | 131 | 697 | S-80 | 2.0 " | No | 94.03.68.150.06.0 |  | 3985 | PD-303B
02-VSTP109 | LP STEAM INLET PIPE DRAIN MANUAL ISOLATION | 02-1"-STP1069-1DAA1A-2.0 "EIC | 1" | Gate valve | STP | 1DAA1A | Steam/Water | CL800 | SWE | SWE | 131 | 697 | S-80 | 2.0 " | No | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 3986 | PD-303B
02-VSTP110 | INSTRUMENT | 02-0.75"-STP1014-1BAB1A-1.5 "EOC | 0.75" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 3987 | PD-304B
02-VSTP111 | INSTRUMENT | 02-2"-STP1016-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 3988 | PD-304B
02-VSTP112 | INSTRUMENT | 02-2"-STP1017-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 3989 | PD-304B
02-VSTP113 | HP ST DRAINS TANK DRAIN ISOLATION | 02-6"-STP1006-1BAA1A-1.0 "MOH | 6" | Gate valve | STP | 1BAA1A | Water | CL150 | RFFE | RFFE | 50 | 240 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | FLEXIBLE WEDGE | 3990 | PD-304B
02-VSTP114 | DRAIN | 02-0.75"-STP1006-1BAA1A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA1A | Water | CL800 | SWE | SWE | 50 | 240 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 3991 | PD-304B
02-VSTP115 | HP ST DRAINS TANK DRAIN ISOLATION | 02-6"-STP1018-1BCA2A-1.0 "MOH | 6" | Gate valve | STP | 1BCA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE, TWO PHASE FLOW, 6% STEAM FLASHING | 3992 | PD-304B
02-VSTP116 | DRAIN | 02-2"-STP1019-1BAB1A-1.5 "EOH | 2" | Gate valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 3993 | PD-304B
02-VSTP117 | GLAND STEAM CONDENSER DRAIN ISOLATION | 02-0.75"-STP1075-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | VACUUM SERVICE | 3994 | PD-306B
02-VSTP118 | GLAND STEAM CONDENSER DRAIN ISOLATION | 02-0.75"-STP1048-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | VACUUM SERVICE | 3995 | PD-306B
02-VSTP119 | GSC EMERGENCY LOOP SEAL DRAIN ISOLATION | 02-2"-STP1045-1BAA1A-1.0 "MIC | 2" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 3996 | PD-302B
02-VSTP120 | GLAND STEAM CONDENSER STEAM TRAP DRAIN ISOLATION | 02-2"-STP1053-1BAA1A-1.0 "MIC | 2" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 3997 | PD-302B
02-VSTP121 | GLAND STEAM CONDENSER STEAM TRAP DRAIN ISOLATION | 02-2"-STP1053-1BAA1A-1.0 "MIC | 2" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 3998 | PD-302B
02-VSTP122 | GLAND STEAM CONDENSER STEAM TRAP STRAINER DRAIN ISOLATION | 02-1"-STP1053-1BAA1A-1.0 "MIC | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 3999 | PD-302B
02-VSTP123 | GLAND STEAM CONDENSER STEAM TRAP BYPASS THROTTLIING | 02-2"-STP1116-1BAA1A-1.0 "MIC | 2" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 4000 | PD-302B
02-VSTP124 | GSC FAN EXHAUST DRAIN ISOLATION | 02-0.75"-STP1103-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H | VACUUM SERVICE | 4001 | PD-306B
02-VSTP125 | GSC FAN EXHAUST CHECK VALVE | 02-6"-STP1027-1BAA2A-1.0 "MIC | 6" | Check valve | STP | 1BAA2A | AIR | CL150 | WAFER | WAFER | 15 | 212 | S-40 | 1.0 " | No | 94.03.68.150.03.2H | DUAL PLATE CHECK VALVE, FLOW- 250 SCFM (FlUID- AIR), CRACKING PRESSURE <0.075 PSID IN VERTICAL (FLOW UP) ORIENTATION | 4002 | PD-302B
02-VSTP126 | GSC EXHAUST LOOP SEAL DRAIN ISOLATION | 02-0.75"-STP1104-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.02.3H |  | 4003 | PD-306B
02-VSTP127 | GLAND STEAM SPILLOVER CONTROL VALVE ISOLATION | 02-8"-STP1065-1DAA1A-3.0 "EIC | 8" | Gate valve | STP | 1DAA1A | Steam | CL300 | RFFE | RFFE | 100 | 797 | S-40 | 3.0 " | No | 94.03.68.150.03.1H | DOUBLE DISC WEDGE, 3-WAY DRAIN, VACUUM SERVICE | 4004 | PD-300B
02-VSTP128 | GSC FAN EXHAUST CHECK VALVE | 02-6"-STP1026-1BAA2A-1.0 "MIC | 6" | Check valve | STP | 1BAA2A | AIR | CL150 | WAFER | WAFER | 15 | 212 | S-40 | 1.0 " | No | 94.03.68.150.03.2H | DUAL PLATE CHECK VALVE, FLOW- 250 SCFM (FlUID- AIR), CRACKING PRESSURE <0.075 PSID IN VERTICAL (FLOW UP) ORIENTATION | 4005 | PD-302B
02-VSTP129 | GLAND STEAM SPILLOVER CONTROL VALVE ISOLATION | 02-12"-STP1065-1DAA1A-3.5 "EIC | 12" | Gate valve | STP | 1DAA1A | Steam | CL300 | RFFE | RFFE | 100 | 797 | S-STD | 3.5 " | No | 94.03.68.150.03.2H | DOUBLE DISC WEDGE, 3-WAY DRAIN, VACUUM SERVICE | 4006 | PD-300B
02-VSTP130 | DRAIN | 02-0.75"-STP1003-1BAA1A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA1A | Water | CL800 | SWE | SWE | 50 | 240 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4007 | PD-304B
02-VSTP131 | INSTRUMENT | 02-1"-STP1655-1DAA1A-2.0 "EIC | 1" | Globe valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H |  | 4008 | PD-300B
02-VSTP132 | GLAND STEAM SPILLOVER CONTROL VALVE BYPASS | 02-6"-STP1653-1DAA1A-3.0 "EIC | 6" | Globe valve | STP | 1DAA1A | Steam | CL300 | RFFE | RFFE | 100 | 797 | S-40 | 3.0 " | No | 94.03.68.150.03.1H | VACUUM SERVICE, THROTTLING, GEAR OPERATOR | 4009 | PD-300B
02-VSTP133 | INSTRUMENT | 02-1"-STP1655-1DAA1A-2.0 "EIC | 1" | Globe valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H |  | 4010 | PD-300B
02-VSTP134 | INSTRUMENT | 02-2"-STP1001-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 4011 | PD-304B
02-VSTP135 | INSTRUMENT | 02-2"-STP1005-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 4012 | PD-304B
02-VSTP136 | INSTRUMENT | 02-0.75"-STP1052-1BAB1A-1.5 "EOC | 0.75" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | No | 94.03.68.150.06.0 |  | 4013 | PD-304B
02-VSTP137 | GLAND STEAM CONDENSER STEAM TRAP EQUALIZING ISOLATION | 02-1"-STP1067-1BAA1A-1.0 "MIC | 1" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 4014 | PD-302B
02-VSTP138 | DRAIN ISOLATION | 02-1"-STP1015-1BAA1A-2.0 "EII | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.3H |  | 4015 | PD-300B
02-VSTP139 | DRAIN ISOLATION | 02-1"-STP1062-1BAA1A-2.0 "EIC | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 15 | 797 | S-80 | 2.0 " | No | 94.03.68.150.02.3H |  | 4016 | PD-302B
02-VSTP140 | DRAIN ISOLATION | 02-1"-STP1054-1DBB1A-3.5 "EIC | 1" | Gate valve | STP | 1DBB1A | Steam/Water | CL800 | SWE | SWE | 15 | 1076 | S-80 | 3.5 " | No | 94.03.68.150.02.3H |  | 4017 | PD-302B
02-VSTP141 | INSTRUMENT | 02-0.75"-STP1149-1BAB1A-1.0 "MOC | 0.75" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | No | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4018 | PD-305B
02-VSTP142 | INSTRUMENT | 02-0.75"-STP1189-1BAB1A-1.0 "MOC | 0.75" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | No | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4019 | PD-305B
02-VSTP143 | INSTRUMENT | 02-2"-STP1091-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4020 | PD-305B
02-VSTP144 | INSTRUMENT | 02-2"-STP1097-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4021 | PD-305B
02-VSTP145 | DRAIN ISOLATION | 02-1"-STP1039-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 4022 | PD-302B
02-VSTP146 | DRAIN ISOLATION | 02-1"-STP1023-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 4023 | PD-302B
02-VSTP147 | DRAIN ISOLATION | 02-1"-STP1033-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 4024 | PD-302B
02-VSTP148 | INSTRUMENT | 02-2"-STP1074-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4025 | PD-305B
02-VSTP149 | INSTRUMENT | 02-2"-STP1072-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4026 | PD-305B
02-VSTP150 | INSTRUMENT | 02-2"-STP1098-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4027 | PD-305B
02-VSTP151 | INSTRUMENT | 02-2"-STP1099-1BAB1A-1.0 "MOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4028 | PD-305B
02-VSTP152 | DRAIN | 02-2"-STP1209-1BAB1A-1.0 "MOH | 2" | Gate valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 260 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4029 | PD-305B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 4030 | P&ID
02-VSTP153 | DRAIN ISOLATION | 02-1"-STP1024-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 4031 | PD-302B
02-VSTP154 | LP STEAM DRAINS PUMP A SUCTION ISOLATION | 02-1"-STP1049-1BAA1A-1.0 "MIC | 1" | Ball valve | STP | 1BAA1A | Steam | CL600 | SWE | SWE | 15 | 248 | S-80 | 1.0 " | No | 94.03.68.150.06.0 |  | 4032 | PD-302B
02-VSTP155 | INSTRUMENT | 02-0.75"-STP1106-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4033 | PD-306B
02-VSTP156 | INSTRUMENT | 02-0.75"-STP1107-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4034 | PD-306B
02-VSTP157 | VENT | 02-0.75"-STP1081-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4035 | PD-306B
02-VSTP158 | DRAIN | 02-0.75"-STP1108-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4036 | PD-306B
02-VSTP159 | GLAND STEAM MIST SEPARATOR DRAIN ISOLATION | 02-1"-STP1008-1BAA1A-1.0 "EIC | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 100 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 4037 | PD-300B
02-VSTP160 | INSTRUMENT | 02-0.75"-STP1102-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4038 | PD-306B
02-VSTP161 | LP STEAM DRAINS PUMP A VENT ISOLATION | 02-0.75"-STP1071-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4039 | PD-306B
02-VSTP162 | INSTRUMENT | 02-0.75"-STP1085-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4040 | PD-306B
02-VSTP163 | LP STEAM DRAINS PUMP A DISCHARGE CHECK VALVE | 02-6"-STP1085-1BAA2A-1.0 "MOH | 6" | Check valve | STP | 1BAA2A | Water | CL150 | RFFE | RFFE | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, SWING CHECK, VERTICAL INSTALLATION, MAX FLOW- 700 GPM, MIN FLOW- 450 GPM | 4041 | PD-306B
02-VSTP164 | DRAIN | 02-0.75"-STP1085-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4042 | PD-306B
02-VSTP165 | LP STEAM DRAINS PUMP A DISCHARGE ISOLATION | 02-6"-STP1085-1BAA2A-1.0 "MOH | 6" | Gate valve | STP | 1BAA2A | Water | CL150 | RFFE | RFFE | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE | 4043 | PD-306B
02-VSTP166 | VENT | 02-0.75"-STP1085-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4044 | PD-306B
02-VSTP167 | GLAND STEAM MIST SEPARATOR DRAIN ORIFICE BYPASS | 02-1"-STP1115-1BAA1A-1.0 "EIC | 1" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 100 | 392 | S-80 | 1.0 " | No | 94.03.68.150.02.3H | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE | 4045 | PD-300B
02-VSTP168 | INSTRUMENT | 02-0.75"-STP1109-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4046 | PD-306B
02-VSTP169 | INSTRUMENT | 02-0.75"-STP1110-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4047 | PD-306B
02-VSTP170 | VENT | 02-0.75"-STP1083-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4048 | PD-306B
02-VSTP171 | DRAIN | 02-0.75"-STP1114-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4049 | PD-306B
02-VSTP172 | PRIMING CONNECTION ISOLATION | 02-0.75"-STP1054-1DBB1A-3.0 "EIC | 0.75" | Gate valve | STP | 1DBB1A | Steam/Water | CL800 | SWE | SWE | 15 | 1076 | S-80 | 3.0 " | No | 94.03.68.150.02.1H |  | 4050 | PD-302B
02-VSTP173 | INSTRUMENT | 02-0.75"-STP1105-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4051 | PD-306B
02-VSTP174 | LP STEAM DRAINS PUMP B VENT ISOLATION | 02-0.75"-STP1073-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4052 | PD-306B
02-VSTP175 | INSTRUMENT | 02-0.75"-STP1084-1BAA2A-1.0 "MOH | 0.75" | Globe valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4053 | PD-306B
02-VSTP176 | LP STEAM DRAINS PUMP B DISCHARGE CHECK VALVE | 02-6"-STP1084-1BAA2A-1.0 "MOH | 6" | Check valve | STP | 1BAA2A | Water | CL150 | RFFE | RFFE | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, SWING CHECK, VERTICAL INSTALLATION, MAX FLOW- 700 GPM, MIN FLOW- 450 GPM | 4054 | PD-306B
02-VSTP177 | DRAIN | 02-0.75"-STP1084-1BAA2A-1.0 "MOH | 0.75" | Gate valve | STP | 1BAA2A | Water | CL800 | SWE | SWE | 80 | 170 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 | RATED FOR VACUUM SERVICE | 4055 | PD-306B
02-VSTP178 | LP STEAM DRAINS PUMP B DISCHARGE ISOLATION | 02-6"-STP1084-1BAA2A-1.0 "MOH | 6" | Gate valve | STP | 1BAA2A | Water | CL150 | RFFE | RFFE | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE | 4056 | PD-306B
02-VSTP179 | GSC FAN EXHAUST ISOLATION | 02-6"-STP1026-1BAA2A-1.0 "MIC | 6" | Butterfly valve | STP | 1BAA2A | AIR | CL150 | LUGGED | LUGGED | 15 | 212 | S-40 | 1.0 " | No | 94.03.68.150.04.1 |  | 4057 | PD-302B
02-VSTP180 | GSC FAN EXHAUST ISOLATION | 02-6"-STP1027-1BAA2A-1.0 "MIC | 6" | Butterfly valve | STP | 1BAA2A | AIR | CL150 | LUGGED | LUGGED | 15 | 212 | S-40 | 1.0 " | No | 94.03.68.150.04.1 |  | 4058 | PD-302B
02-VSTP181 | GLAND STEAM MIST SEPARATOR DRAIN THROTTLE | 02-1"-STP1008-1BAA1A-1.0 "EIC | 1" | Globe valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 100 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 4059 | PD-300B
02-VSTP182 | GLAND STEAM MIST SEPARATOR DRAIN ISOLATION | 02-1"-STP1008-1BAA1A-1.0 "EIC | 1" | Gate valve | STP | 1BAA1A | Steam | CL800 | SWE | SWE | 100 | 392 | S-80 | 1.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 4060 | PD-300B
02-VSTP183 | GLAND STEAM HEADER DRAIN ISOLATION | 02-1"-STP1032-1DAA1A-2.0 "EIC | 1" | Gate valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 4061 | PD-300B
02-VSTP184 | GLAND STEAM HEADER DRAIN THROTTLE | 02-1"-STP1032-1DAA1A-2.0 "EIC | 1" | Globe valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 4062 | PD-300B
02-VSTP185 | GLAND STEAM HEADER DRAIN ISOLATION | 02-1"-STP1032-1DAA1A-2.0 "EIC | 1" | Gate valve | STP | 1DAA1A | Steam | CL800 | SWE | SWE | 100 | 797 | S-80 | 2.0 " | No | 94.03.68.150.06.2H | VACUUM SERVICE | 4063 | PD-300B
02-VSTP195 | INSTRUMENT | 02-2"-STP1100-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 4064 | PD-304B
02-VSTP196 | INSTRUMENT | 02-2"-STP1101-1BAB1A-1.5 "EOH | 2" | Globe valve | STP | 1BAB1A | Steam | CL800 | SWE | SWE | 50 | 750 | S-80 | 1.5 " | Yes | 94.03.68.150.06.0 |  | 4065 | PD-304B
02-VSTP370 | HP ST DRAINS TANK DRAIN ISOLATION | 02-6"-STP1002-1BCA2A-1.0 "MOH | 6" | Gate valve | STP | 1BCA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-10S | 1.0 " | Yes | 94.03.68.150.03.0 | RATED FOR VACUUM SERVICE, FLEXIBLE WEDGE, TWO PHASE FLOW, 6% STEAM FLASHING | 4066 | PD-304B
02-VSTP371 | HP ST DRAINS TANK DRAIN ISOLATION | 02-6"-STP1003-1BAA1A-1.0 "MOH | 6" | Gate valve | STP | 1BAA1A | Water | CL150 | RFFE | RFFE | 50 | 240 | S-40 | 1.0 " | Yes | 94.03.68.150.03.0 | FLEXIBLE WEDGE | 4067 | PD-304B
02-VSTP386 | CONDENSATE RECEIVER TANK ISOLATION | 02-6"-STP1085-1BAA2A-1.0 "MOH | 6" | Butterfly valve | STP | 1BAA2A | Water | CL150 | LUGGED | LUGGED | 80 | 170 | S-40 | 1.0 " | Yes | 94.03.68.150.04.0 | RATED FOR VACUUM SERVICE | 4068 | PD-306B
02-VSWS100 | BEARING FLUSH ISOLATION | 02-1"-SWS1031-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4069 | PD-090B
02-VSWS101 | INSTRUMENT | 02-0.5"-SWS1192-1BAB3A-1.0 "MOH | 0.5" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4070 | PD-090B
02-VSWS102 | INSTRUMENT | 02-0.5"-SWS1192-1BAB3A-1.0 "MOH | 0.5" | Globe valve | SWS | 1BAB3A | Water | CL800 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4071 | PD-090B
02-VSWS103 | VACUUM PUMP MAKEUP ISOLATION | 02-1"-SWS1022-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4072 | PD-393
02-VSWS104 | VACUUM PUMP MAKEUP ISOLATION | 02-1"-SWS1021-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4073 | PD-393
02-VSWS105 | VACUUM PUMP MAKEUP ISOLATION | 02-1"-SWS1020-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4074 | PD-393
02-VSWS106 | FIN TUBE CLEANING SKID ISOLATION | 02-2"-SWS1180-1BAH1A-1.0 "MOH | 2" | Ball valve | SWS | 1BAH1A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4075 | PD-393
02-VSWS108 | DRAIN | 02-0.75"-SWS1192-1BAB3A-1.0 "MOH | 0.75" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4076 | PD-090B
02-VSWS109 | UNIT 2 HRSG BLOWDOWN SUMP QUENCH ISOLATION | 02-3"-SWS1016-1BAH1A-1.0 "MOH | 3" | Ball valve | SWS | 1BAH1A | Water | CL150 | RFFE | RFFE | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.03.0 |  | 4077 | PD-090B
02-VSWS110 | DRAIN | 02-0.75"-SWS1016-1BAB3A-1.0 "MOH | 0.75" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4078 | PD-090B
02-VSWS111 | UNIT 2 HRSG BLOWDOWN TANK/SUMP QUENCH ISOLATION | 02-6"-SWS1192-1BAH1A-1.0 "MOH | 6" | Butterfly valve | SWS | 1BAH1A | Water | CL150 | LUGGED | LUGGED | 145 | 110 | S-STD | 1.0 " | Yes | 94.03.68.150.04.0 |  | 4079 | PD-090B
02-VSWS115 | VACUUM PUMP MAKEUP ISOLATION | 02-1"-SWS1015-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4080 | PD-393
02-VSWS118 | VACUUM PUMP MAKEUP ISOLATION | 02-1"-SWS1018-1BAB3A-1.0 "MOH | 1" | Ball valve | SWS | 1BAB3A | Water | CL600 | SWE | SWE | 145 | 110 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4081 | PD-393
02-VWDR100 | OIL IN WATER ANALYZER ISOLATION VALVE | 02-0.75"-WDR1179-1BAB2A-1.0 "MOH | 0.75" | Globe valve | WDR | 1BAB2A | Water | CL800 | SWE | SWE | 50 | 200 | S-80 | 1.0 " | Yes | 94.03.68.150.06.3H |  | 4082 | PD-960B
02-VWDR237 | VENT | 02-0.75"-WDR1179-1BAB2A-1.0 "MOH | 0.75" | Globe valve | WDR | 1BAB2A | Water | CL800 | SWE | SWE | 50 | 200 | S-80 | 1.0 " | Yes | 94.03.68.150.06.0 |  | 4083 | PD-960B
02-YV-BFW309 | TCA COOLER INLET EMERGENCY SHUTOFF | 02-6"-BFW1028-1HAC2A-1.5 "EOH | 6" | Globe control valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS | 1.5 " | Yes | 94.03.68.100.01.2 |  | 4084 | PD-063B
02-YV-BFW319 | CTA COOLER BFW SUPPLY STARTUP VALVE | 02-1"-BFW1377-1HAC2A-1.0 "EOH | 1" | Globe control valve | BFW | 1HAC2A | Water | CL2500 | SWE | SWE | 4100 | 370 | S-160 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 4085 | PD-063B
02-YV-BFW409 | FGH UPSTREAM BFW EMERGENCY SHUTOFF | 02-4"-BFW1438-1FAC1A-1.5 "EOH | 4" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 589 | S-80 | 1.5 " | Yes | 94.03.68.100.01.2 |  | 4086 | PD-064B
02-YV-BFW419 | FG HX BFW SUPPLY STARTUP VALVE | 02-1"-BFW1454-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 4087 | PD-064B
02-YV-BFW445 | FGH BFW OUTLET EMERGENCY SHUTOFF | 02-4"-BFW1008-1FAC1A-1.0 "EOH | 4" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 589 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 4088 | PD-064B
02-YV-BFW705 | HPS TA SPRAY SUPPLY AUTOMATIC BLOCK | 02-3"-BFW1150-1HAC2A-1.0 "EOH | 3" | Globe control valve | BFW | 1HAC2A | Water | CL2500 | BE | BE | 4100 | 370 | S-XXS |  | Yes | 94.03.68.100.01.0 |  | 4089 | PD-020B
02-YV-BFW715 | HPS BYPASS SPRAY SUPPLY AUTOMATIC BLOCK | 02-3"-BFW1006-1FAC1A-1.0 "EOH | 3" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.100.01.0 |  | 4090 | PD-020B
02-YV-BFW735 | HRH SPRAY SUPPLY AUTOMATIC BLOCK | 02-3"-BFW1108-1FAC1A-1.0 "EOH | 3" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | BE | BE | 1400 | 370 | S-40 | 1.0 " | Yes | 94.03.68.100.01.0 |  | 4091 | PD-034B
02-YV-BFW745 | CRH LETDOWN PCV SPRAY AUTOMATIC BLOCK | 02-1"-BFW1036-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 4092 | PD-124B
02-YV-BFW757 | CRH LETDOWN ATTEMPERATOR SPRAY AUTOMATIC BLOCK | 02-1"-BFW1699-1FAC1A-1.0 "EOH | 1" | Globe control valve | BFW | 1FAC1A | Water | CL1500 | SWE | SWE | 1400 | 370 | S-80 | 1.0 " | Yes | 94.03.68.100.01.2 |  | 4093 | PD-124B
02-YV-CND441 | CND SYSTEM EMERGENCY DUMP VALVE | 02-3"-CND1103-1EAA2A-1.0 "MOH | 3" | Globe control valve | CND | 1EAA2A | Water | CL600 | BE | BE | 790 | 290 | S-40 | 1.0 " | Yes | 94.03.68.100.02.1 |  | 4094 | PD-053B
Tag Number | Description | Line Number | Size (in) | Valve Type | System | Pipe Spec | Working Fluid | Rating | End Prep1 | End Prep2 | Design Press (psig) | Design Temp (F) | Valve Schedule | Insulation Thickness | Heat Traced | Purchase Spec | Comments | 4095 | P&ID
02-YV-CND509 | ECA COOLER LOOP SUPPLY AUTOMATIC ISOLATION | 02-6"-CND1031-1EAA1A-1.0 "EOH | 6" | Globe control valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.100.02.2 | ON/OFF SOLENOID, OPEN AND CLOSED LIMIT SWITCHES, FAIL OPEN | 4096 | PD-054B
02-YV-CND571 | ECA COOLER LOOP RETURN AUTOMATIC ISOLATION | 02-6"-CND1039-1EAA1A-1.0 "EOH | 6" | Globe control valve | CND | 1EAA1A | Water | CL600 | BE | BE | 850 | 302 | S-40 | 1.0 " | Yes | 94.03.68.100.02.2 | ON/OFF SOLENOID, OPEN AND CLOSED LIMIT SWITCHES, FAIL OPEN | 4097 | PD-054B
02-YV-CND702 | HRH BYPASS SPRAY SUPPLY AUTOMATIC BLOCK | 02-4"-CND1256-1EAA2A-1.0 "MIC | 4" | Globe control valve | CND | 1EAA2A | Water | CL600 | RFFE | RFFE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.100.01.0 |  | 4098 | PD-034B
02-YV-CND705 | CRH VENTILATOR SPRAY AUTOMATIC BLOCK | 02-3"-CND1062-1EAA2A-1.0 "MIC | 3" | Globe control valve | CND | 1EAA2A | Water | CL600 | RFFE | RFFE | 790 | 170 | S-40 | 1.0 " | No | 94.03.68.100.01.3 |  | 4099 | PD-030B
02-YV-CND721 | GLAND STEAM DSH SPRAY AUTOMATIC BLOCK | 02-1"-CND1181-1EAA2A-1.0 "MIC | 1" | Globe control valve | CND | 1EAA2A | Water | CL600 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.100.02.2 |  | 4100 | PD-300B
02-YV-CND725 | LP BYPASS VALVE SPRAY SUPPLY AUTOMATIC BLOCK | 02-1"-CND1459-1EAA2A-1.0 "MIC | 1" | Globe control valve | CND | 1EAA2A | Water | CL800 | SWE | SWE | 790 | 170 | S-80 | 1.0 " | No | 94.03.68.100.01.0 |  | 4101 | PD-040B
02-YV-DWS719 | CONDENSER EMERGENCY MAKEUP ON/OFF | 02-6"-DWS1006-1BCA2A-1.0 "MOH | 6" | Butterfly control valve | DWS | 1BCA2A | Water | CL150 | RFFE | RFFE | 170 | 110 | S-10S | 1.0 " | Yes | 94.03.68.100.02.2 |  | 4102 | PD-050B
02-YV-STP131 | HP ST DRAINS TANK DRAIN ON/OFF | 02-6"-STP1018-1BCA2A-1.0 "MOH | 6" | Globe control valve | STP | 1BCA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-10S | 1.0 " | Yes | 94.03.68.100.02.3 | RATED FOR VACCUM SERVICE, LESS THAN 5 SEC TO ACTUATE, SEE VALVE DATASHEET FOR MORE DETAILS | 4103 | PD-304B
02-YV-STP132 | HP ST DRAINS TANK DRAIN ON/OFF | 02-6"-STP1002-1BCA2A-1.0 "MOH | 6" | Globe control valve | STP | 1BCA2A | Water | CL150 | RFFE | RFFE | 50 | 170 | S-10S | 1.0 " | Yes | 94.03.68.100.02.3 | RATED FOR VACCUM SERVICE, LESS THAN 5 SEC TO ACTUATE, SEE VALVE DATASHEET FOR MORE DETAILS | 4104 | PD-304B
02-YV-WDR110 | UNIT 2 OWS AUTOMATIC ISOLATION VALVE | 02-6"-WDR1179-1BAB2A-1.0 "MOH | 6" | Butterfly control valve | WDR | 1BAB2A | Water | CL150 | RFFE | RFFE | 50 | 200 | S-40 | 1.0 " | Yes | 94.03.68.100.02.2 |  | 4105 | PD-960B

## HRSG
Rev+A2:V2 | Item Tag | Designation | Inlet Pipe Tag | Outlet Pipe Tag | Fluid | Act Type (Note 1) | Fail safe position (Note 2) | Nominal Pipe Size In (Inch) | Nominal Pipe Size Out (Inch) | Valve Type | Pipe Material In | Pipe Material Out | Vlv Material | MAWP [psig] | Design Temp. [°F] | MAWP [barg] | Design Temp. [°C] | Valve Class In | Valve Class Out | Pipe End In | Pipe End Out | Remarks | Hydrotest Pressure [psig] | Hydrotest Pressure [barg] | Hydrotest Number | Cavity Over Pressure Protection (NOTE 3) | Supplier | John Cockerill Valve Drawing Number | WBS Number | Original ID | John Cockerill PID Number
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 4106 | 2080_00003‐1
D | 01‐PRV‐HLS998 | LP DRUM PRESSURE RELIEF VALVE 2 | LP DRUM | HLS9704 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23211 | 23.03 | 4107 | 2080_00003‐1
D | 01‐PRV‐HLS999 | LP STEAM OUTLET PRESSURE RELIEF VALVE | HLS9165 | HLS9706 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 623 | 9 | 328.5 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23213 | 23.03 | 4108 | 2080_00003‐2
D | 01‐PRV‐HIS995 | IP ECONOMIZER INLET PRESSURE RELIEF VALVE | HIS9103 | HIS9701 | Water | NA | NA | 2" | 3" | PRV | SA‐106 B | SA‐106 B | SA‐351 Gr CF8M | 1400 | 550 | 96.5 | 288 | 1500 | 300 | FL | FL |  | 2100 | 145 | 9 & 3 | ‐ | Trillium | 2080_23228 | 23.03 | 4109 | 2080_00004‐1
D | 01‐PRV‐HIS997 | IP DRUM PRESSURE RELIEF VALVE 1 | IP DRUM | HIS9702 | Steam | NA | NA | 3" | 4" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 493 | 43 | 256.1 | 300 | 150 | FL | FL |  | 935 | 65 | 4 | ‐ | Trillium | 2080_23222 | 23.03 | 4110 | 2080_00004‐2
D | 01‐PRV‐HIS998 | IP DRUM PRESSURE RELIEF VALVE 2 | IP DRUM | HIS9703 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 493 | 43 | 256.1 | 300 | 150 | FL | FL |  | 935 | 65 | 4 | ‐ | Trillium | 2080_23221 | 23.03 | 4111 | 2080_00004‐2
D | 01‐PRV‐HIS999 | IP STEAM OUTLET PRESSURE RELIEF VALVE | HIS9146 | HIS9704 | Steam | NA | NA | 3" | 4" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 622 | 43 | 327.6 | 300 | 150 | FL | FL |  | 935 | 65 | 4 | ‐ | Trillium | 2080_23223 | 23.03 | 4112 | 2080_00004‐3
D | 01‐PRV‐HRS997 | COLD REHEAT PRESSURE RELIEF VALVE 1 | HRS9192 | HRS9705 | Steam | NA | NA | 6" | 10" | PRV | SA‐335 P11 | SA‐335 P11 | SA‐216 Gr WCC | 624 | 752 | 43 | 400.2 | 600 | 150 | FL | FL |  | 935 | 65 | 5 | ‐ | Trillium | 2080_23225 | 23.03 | 4113 | 2080_00004‐4
D | 01‐PRV‐HRS998 | COLD REHEAT PRESSURE RELIEF VALVE 2 | HRS9192 | HRS9706 | Steam | NA | NA | 8" | 2 x 10" | PRV | SA‐335 P11 | SA‐335 P11 | SA‐216 Gr WCC | 624 | 752 | 43 | 400.2 | 600 | 150 | FL | FL |  | 935 | 65 | 5 | ‐ | Trillium | 2080_23224 | 23.03 | 4114 | 2080_00004‐4
D | 01‐PRV‐HRS999 | HOT REHEAT PRESSURE RELIEF VALVE | HRS9195 | HRS9707 | Steam | NA | NA | 6" | 8" | PRV | SA‐335 P91 | SA‐335 P91 | SA‐351 Gr CF8M | 624 | 1096 | 43 | 591.1 | 600 | 300 | FL | FL |  | 935 | 65 | 5 | ‐ | Trillium | 2080_23226 | 23.03 | 4115 | 2080_00004‐4
D | 01‐PRV‐HHS997 | HP DRUM PRESSURE RELIEF VALVE 1 | HP DRUM | HHS9701 | Steam | NA | NA | 2.5" | 6" | PRV | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2741 | 683 | 189 | 361.5 | 2500 | 300 | FL | FL |  | 4112 | 284 | 7 | ‐ | Trillium | 2080_23232 | 23.03 | 4116 | 2080_00005‐2
D | 01‐PRV‐HHS998 | HP DRUM PRESSURE RELIEF VALVE 2 | HP DRUM | HHS9702 | Steam | NA | NA | 3" | 6" | PRV | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2741 | 683 | 189 | 361.5 | 2500 | 300 | FL | FL |  | 4112 | 284 | 7 | ‐ | Trillium | 2080_23231 | 23.03 | 4117 | 2080_00005‐2
D | 01‐PRV‐HHS999 | HP STEAM OUTLET PRESSURE RELIEF VALVE | HHS9220 | HHS9703 | Steam | NA | NA | 3" | 6" | PRV | SA‐335 P91 | SA‐335 P91 | SA‐217 Gr C12A | 2534 | 1098 | 174.7 | 592 | 2500 | 300 | FL | FL |  | 4112 | 284 | 7 | ‐ | Trillium | 2080_23233 | 23.03 | 4118 | 2080_00005‐3
E | 01‐PRV‐HLS901 | PREHEATER EXT HEAT EXCHANGER PRESSURE RELIEF VALVE | HLS9174 | HLS9701 | Water | NA | NA | 1" | 2" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 455 | 41.4 | 235 | 300 | 300 | FL | FL |  | 901 | 62 | 9 & 1 | ‐ | Trillium | 2080_23201 | 23.03 | 4119 | 2080_00006‐1
E | 01‐PRV‐HLS902 | PREHEATER EXT HEAT EXCHANGER PRESSURE RELIEF VALVE | HLS9113 | HLS9702 | Water | NA | NA | 1" | 2" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 490 | 41.4 | 254.7 | 300 | 300 | FL | FL |  | 901 | 62 | 9 & 1 | ‐ | Trillium | 2080_23202 | 23.03 | 4120 | 2080_00006‐1
D | 01‐PRV‐HLS994 | PREHEATER INLET PILOT OPERATED RELIEF VALVE | HLS9104 | HLS9193 | Water | NA | NA | 6" | 8" | PRV | SA‐106 B | SA‐106 B | SA‐351 Gr CF8M | 600 | 455 | 41.4 | 235 | 600 | 150 | FL | FL |  | 901 | 62 | 9 & 1 | ‐ | Trillium | 2080_23207 | 23.03 | 4121 | 2080_00006‐1
D | 01‐LCV‐HLS901 | LP DRUM LEVEL CONTROL VALVE | HLS9118 | HLS9126 | Water | POVCTRL | FSC | 12" | 12" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 489 | 41.4 | 253.8 | 2500 | 2500 | BW | BW | EWT CAV III Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23416 | 23.04 | 4122 | 2080_00003‐1
D | 01‐PCV‐HLS901 | LP SPARGING STEAM CONTROL VALVE | HLS9130 | HLS9178 | Steam | POVCTRL | LSC | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 425 | 454 | 29.3 | 234.4 | 600 | 600 | SW | SW | ES Valve Body | 638 | 44 | 2 & 8 | ‐ | Fisher | 2080_23418 | 23.04 | 4123 | 2080_00003‐1
D | 01‐LCV‐HIS901 | IP DRUM LEVEL CONTROL VALVE | HIS9115 | HIS9116 | Water | POVCTRL | FSC | 3" | 3" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW | HPT Valve Body | 2100 | 145 | 3 | ‐ | Fisher | 2080_23407 | 23.04 | 4124 | 2080_00004‐2
D | 01‐PCV‐HIS901 | IP SPARGING STEAM CONTROL VALVE | HIS9141 | HIS9107 | Steam | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 656 | 498 | 45.2 | 259 | 600 | 600 | SW | SW | ES Valve Body | 935 | 65 | 4 | ‐ | Fisher | 2080_23410 | 23.04 | 4125 | 2080_00004‐2
D | 01‐PCV‐HIS902 | IP TO LP PEGGING STEAM CONTROL VALVE | HIS9202 | HIS9201 | Steam | POVCTRL | FSC | 3" | 3" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 502 | 43 | 261.1 | 600 | 600 | BW | BW | ET Valve Body | 935 | 65 | 2 & 4 | ‐ | Fisher | 2080_23406 | 23.04 | 4126 | 2080_00004‐2
D | 01‐PCV‐HIS903 | IP STEAM OUTLET BACK PRESSURE CONTROL VALVE | HIS9190 | HIS9148 | Steam | POVCTRL | FSO | 8" | 8" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 622 | 43 | 327.6 | 600 | 600 | BW | BW | ED Valve Body | 935 | 65 | 4 | ‐ | Fisher | 2080_23411 | 23.04 | 4127 | 2080_00004‐3
D | 01‐LCV‐HHS901 | HP DRUM LEVEL CONTROL VALVE 1 (25%‐100%) | HHS9103 | HHS9104 | Water | POVCTRL | FSC | 8" | 8" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | HPT Valve Body | 6150 | 424 | 6 | ‐ | Fisher | 2080_23401 | 23.04 | 4128 | 2080_00005‐1
D | 01‐LCV‐HHS902 | HP DRUM LEVEL CONTROL VALVE 2 (0‐30%) | HHS9107 | HHS9108 | Water | POVCTRL | FSC | 4" | 4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | HPT Valve Body | 6150 | 424 | 6 | ‐ | Fisher | 2080_23402 | 23.04 | 4129 | 2080_00005‐1
D | 01‐FCV‐HHS901 | HP SPARGING STEAM CONTROL VALVE | HHS9218 | HHS9221 | Steam | POVCTRL | FSC | 3" | 3" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2773 | 684 | 191.2 | 362.4 | 1500 | 1500 | BW | BW | HPD Valve Body | 4112 | 284 | 7 | ‐ | Fisher | 2080_23405 | 23.04 | 4130 | 2080_00005‐2
D | 01‐FCV‐HHS904 | HP TO IP CASCADING BLOWDOWN CONTROL VALVE | HHS9943 | HHS9944 | Water | NA | NA | 2" | 2" | Angle Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2773 | 684 | 191.2 | 362.4 | 1500 | 1500 | SW | SW | HPAS Valve Body | 4112 | 284 | 9 & 7 | ‐ | Fisher | 2080_23403 | 23.04 | 4131 | 2080_00005‐2
D | 01‐PCV‐HHS902 | HP STEAM OUTLET CONTROL VALVE | HHS9192 | HHS9192 | Steam | POVCTRL | FSC | 12" | 12" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐217 Gr C12A | 2534 | 1098 | 174.7 | 592 | 3200 | 3200 | BW | BW | HPD Valve Body | 4112 | 284 | 7 |  | Fisher | 2080_23421 | 23.04 | 4132 | 2080_00005‐3
D | 01‐TCV‐HLS901 | PREHEATER BYPASS CONTROL VALVE 1 | HLS9170 | HLS9171 | Water | POVCTRL | FSO | 10" | 10" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 345 | 41.4 | 174 | 600 | 600 | BW | BW | EWT Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23412 | 23.04 | 4133 | 2080_00006‐1
D | 01‐TCV‐HLS902 | PREHEATER BYPASS CONTROL VALVE 2 | HLS9117 | HLS9120 | Water | POVCTRL | FSO | 10" | 10" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 345 | 41.4 | 174 | 600 | 600 | BW | BW | EWT Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23413 | 23.04 | 4134 | 2080_00006‐1
D | 01‐TCV‐HLS903 | PREHEATER EXT HEAT EXCHANGER CONTROL VALVE 1 | HLS9121 | HLS9111 | Water | POVCTRL | FSO | 10" | 10" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 490 | 41.4 | 254.7 | 600 | 600 | BW | BW | EWT Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23414 | 23.04 | 4135 | 2080_00006‐1
D | 01‐TCV‐HLS904 | PREHEATER EXT HEAT EXCHANGER CONTROL VALVE 2 | HLS9122 | HLS9112 | Water | POVCTRL | FSO | 10" | 10" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 490 | 41.4 | 254.7 | 600 | 600 | BW | BW | EWT Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23415 | 23.04 | 4136 | 2080_00006‐1
D | 01‐FCV‐HIS904 | IP CONTINUOUS BLOWDOWN CONTROL VALVE | HIS9912 | HBD9108 | Water | NA | NA | 2" | 2" | Angle Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 656 | 498 | 45.2 | 259 | 600 | 600 | SW | SW | EAS Valve Body | 935 | 65 | 9 & 4 | ‐ | Fisher | 2080_23408 | 23.04 | 4137 | 2080_00007‐1
D | 01‐TCV‐HBD901 | BLOWDOWN TANK COOLING WATER CONTROL VALVE | HBD9109 | HBD9110 | Water | POVCTRL | FSC | 4" | 4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 58 | 750 | 4 | 399 | 600 | 600 | BW | BW | ET Valve Body | 78 | 5 | 9 | ‐ | Fisher | 2080_23419 | 23.04 | 4138 | 2080_00007‐1
D | 01‐YCV‐HHS901 | HP INTERMITTENT BLOWDOWN CONTROL VALVE | HHS9947 | HBD9905 | Water | POVCTRL | FSC | 2" | 2" | Angle Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2998 | 696 | 206.7 | 368.9 | 1500 | 1500 | SW | SW | HPAS Valve Body | 4112 | 284 | 9 & 7 | ‐ | Fisher | 2080_23404 | 23.04 | 4139 | 2080_00007‐1
D | 01‐YCV‐HIS901 | IP INTERMITTENT BLOWDOWN CONTROL VALVE | HIS9917 | HBD9910 | Water | POVCTRL | FSC | 2" | 2" | Angle Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 812 | 522 | 56 | 272.2 | 600 | 600 | SW | SW | EAS Valve Body | 935 | 65 | 9 & 4 | ‐ | FIsher | 2080_23409 | 23.04 | 4140 | 2080_00007‐1
D | 01‐YCV‐HLS901 | LP INTERMITTENT BLOWDOWN CONTROL VALVE | HLS9934 | HBD9911 | Water | POVCTRL | FSC | 3" | 3" | Angle Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 196 | 386 | 13.5 | 196.5 | 600 | 600 | SW | SW | EAS Valve Body | 196 | 14 | 9 & 2 | ‐ | Fisher | 2080_23417 | 23.04 | 4141 | 2080_00007‐1
D | 01‐TCV‐HRS901 | REHEAT INTERSTAGE ATTEMPERATOR CONTROL VALVE | HRS9164 | HRS9164 | Water | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 1400 | 374 | 96.5 | 189.9 | 600 | 600 | BW | BW | ES Valve Body | 2100 | 145 | 3 | ‐ | Fisher | 2080_23506 | 23.05 | 4142 | 2080_00004‐4
D | 01‐TCV‐HRS902 | REHEAT FINAL ATTEMPERATOR CONTROL VALVE | BOP | BOP | Water | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 1400 | 374 | 96.5 | 189.9 | 600 | 600 | BW | BW | ET Valve Body | 2100 | 145 | 3 | ‐ | Fisher | 2080_23508 | 23.05 | 4143 | 2080_00004‐4
D | 01‐TCV‐HHS801 | HP INTERSTAGE ATTEMPERATOR CONTROL VALVE | HHS8199 | HHS8199 | Water | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | HPS Valve Body | 6150 | 424 | 6 | ‐ | Fisher | 2080_23502 | 23.05 | 4144 | 2080_00005‐3
D | 01‐TCV‐HHS902 | HP FINAL ATTEMPERATOR CONTROL VALVE | BOP | BOP | Water | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | HPS Valve Body | 6150 | 424 | 6 | ‐ | Fisher | 2080_23504 | 23.05 | 4145 | 2080_00005‐3
D | 01‐VHEH910 | STACK DRAIN | HEH9906 | HEH9906 | Water | NA | NA | 3" | 3" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 15 | 212 | 1 | 100 | 150 | 150 | BW | BW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23008 | 23.21 | 4146 | 2080_00002‐1
D | 01‐VHLS924 | BFP SUCTION | HLS9149 | HLS9149 | Water | NA | NA | 12" | 12" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 162 | 372 | 11.2 | 188.7 | 150 | 150 | BW | BW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23007 | 23.21 | 4147 | 2080_00003‐1
D | 01‐VHLS940 | LP CV ISOLATION | HLS9118 | HLS9118 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 489 | 41.4 | 253.8 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23004 | 23.21 | 4148 | 2080_00003‐1
D | 01‐VHLS941 | LP CV ISOLATION | HLS9126 | HLS9127 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐217 Gr WC6 | 600 | 489 | 41.4 | 253.8 | 300 | 300 | BW | BW |  | 901 | 62 | 2 & 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23006 | 23.21 | 4149 | 2080_00003‐1
D | 01‐VHLS994 | LP STEAM SPARGING CHECK VALVE | HLS9178 | HLS9178 | Steam | NA | NA | 3" | 3" | Check Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCB | 162 | 372 | 11.2 | 188.7 | 300 | 300 | BW | BW | Previous tag 01‐VHLS944 (redundant with other valve) | 196 | 14 | 2 | ‐ | HP Valve | 2080_23002 | 23.21 | 4150 | 2080_00003‐1
D | 01‐VHIS901 | IP FEEDWATER INLET | HIS9100 | HIS9100 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 3 | Bypass Equalizer Type 1 | HP Valve | 2080_23025 | 23.21 | 4151 | 2080_00004‐1
D | 01‐VHIS902 | IP FEEDWATER INLET CHECK VALVE | HIS9106 | HIS9106 | Water | NA | NA | 4" | 4" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23029 | 23.21 | 4152 | 2080_00004‐1
D | 01‐VHIS921 | IP FGH EXTRACTION CHECK VALVE | HIS9114 | HIS9114 | Water | NA | NA | 4" | 4" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23021 | 23.21 | 4153 | 2080_00004‐1
D | 01‐VHIS934 | IP CV ISOLATION VALVE | HIS9113 | HIS9115 | Water | NA | NA | 4" | 4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 3 | Bypass Equalizer Type 1 | HP Valve | 2080_23015 | 23.21 | 4154 | 2080_00004‐2
D | 01‐VHIS935 | IP CV ISOLATION VALVE | HIS9116 | HIS9117 | Water | NA | NA | 4" | 4" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 4 & 3 | Bypass Equalizer Type 4 | HP Valve | 2080_23016 | 23.21 | 4155 | 2080_00004‐2
D | 01‐VHIS975 | IP STEAM SPARGING CHECK VALVE | HIS9107 | HIS9107 | Steam | NA | NA | 3" | 3" | Check Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCB | 656 | 498 | 45.2 | 259 | 300 | 300 | BW | BW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23002 | 23.21 | 4156 | 2080_00004‐2
D | 01‐VHIS978 | IP PEGGING STEAM | HIS9212 | HIS9213 | Steam | NA | NA | 6" | 6" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐217 Gr WC6 | 131 | 365 | 9 | 184.9 | 300 | 300 | BW | BW |  | 196 | 14 | 2 | Bypass Equalizer Type 3 | HP Valve | 2080_23033 | 23.21 | 4157 | 2080_00004‐2
D | 01‐VHIS989 | IP NRV (STOP CHECK) | HIS9146 | HIS9147 | Steam | NA | NA | 8" | 8" | NRV (Stop‐Check) | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 624 | 622 | 43 | 327.6 | 300 SPL | 300 SPL | BW | BW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23003 | 23.21 | 4158 | 2080_00004‐3
D | 01‐VHRS830 | RH INTERSTAGE ATTEMPERATOR SPRAY WATER ISOLATION | HRS9182 | HRS9182 | Water | NA | NA | 2 1/2" | 2 1/2" | Gate Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW | Previously VHRS930 on P&ID | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23013 | 23.21 | 4159 | 2080_00004‐4
D | 01‐VHRS831 | RH INTERSTAGE ATTEMPERATOR SPRAY WATER SWING CHECK VALVE | HRS9182 | HRS9182 | Water | NA | NA | 2 1/2" | 2 1/2" | Check Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW | Previously VHRS931 on P&ID | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23018 | 23.21 | 4160 | 2080_00004‐4
D | 01‐VHHS901 | HP FEEDWATER CONTROL VALVE ISOLATION | HHS9102 | HHS9103 | Water | NA | NA | 12" | 12" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2000 | 2000 | BW | BW |  | 6150 | 424 | 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23024 | 23.21 | 4161 | 2080_00005‐1
D | 01‐VHHS902 | HP FEEDWATER CONTROL VALVE ISOLATION | HHS9104 | HHS9105 | Water | NA | NA | 12" | 12" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2000 | 2000 | BW | BW |  | 6150 | 424 | 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23024 | 23.21 | 4162 | 2080_00005‐1
D | 01‐VHHS903 | HP FEEDWATER CONTROL VALVE ISOLATION | HHS9106 | HHS9107 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW |  | 6150 | 424 | 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23026 | 23.21 | 4163 | 2080_00005‐1
D | 01‐VHHS904 | HP FEEDWATER CONTROL VALVE ISOLATION | HHS9108 | HHS9109 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW |  | 6150 | 424 | 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23026 | 23.21 | 4164 | 2080_00005‐1
D | 01‐VHHS911 | HP FEEDWATER INLET SWING CHECK VALVE | HHS9105 | HHS9105 | Water | NA | NA | 12" | 12" | Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2000 | 2000 | BW | BW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23017 | 23.21 | 4165 | 2080_00005‐1
D | 01‐VHHS948 | HP TCA RETURN TO HP ECONOMIZER ISOLATION | HHS9118 | HHS9118 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 4100 | 705 | 282.7 | 373.9 | 1500 SPL | 1500 SPL | BW | BW |  | 6150 | 424 | with BOP | Bypass Equalizer Type 1 | HP Valve | 2080_23035 | 23.21 | 4166 | 2080_00005‐1
D | 01‐VHHS949 | HP TCA RETURN TO HP ECONOMIZER CHECK | HHS9117 | HHS9118 | Water | NA | NA | 6" | 6" | Check Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 4100 | 705 | 282.7 | 373.9 | 1500 SPL | 1500 SPL | BW | BW |  | 6150 | 424 | with BOP | ‐ | HP Valve | 2080_23036 | 23.21 | 4167 | 2080_00005‐1
D | 01‐VHHS993 | HP STEAM SPARGING CHECK VALVE | HHS9221 | HHS9221 | Steam | NA | NA | 4" | 4" | Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 1500 SPL | 1500 SPL | BW | BW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23020 | 23.21 | 4168 | 2080_00005‐2
D | 01‐VHHS844 | HP INTERSTAGE ATTEMPERATOR SPRAY WATER ISOLATION | HHS8198 | HHS8200 | Water | NA | NA | 2 1/2" | 2 1/2" | Gate Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 4100 | 374 | 282.7 | 189.9 | 2500 LTD | 2500 LTD | BW | BW |  | 6150 | 424 | 7 & 6 | ‐ | HP Valve | 2080_23014 | 23.21 | 4169 | 2080_00005‐3
D | 01‐VHHS845 | HP INTERSTAGE ATTEMPERATOR SPRAY WATER SWING CHECK VALVE | HHS8200 | HHS8201 | Water | NA | NA | 2 1/2" | 2 1/2" | Check Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 4100 | 1032 | 282.7 | 555.6 | 2500 | 2500 | BW | BW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23019 | 23.21 | 4170 | 2080_00005‐3
D | 01‐VHLS901 | LP FEEDWATER INLET CHECK | HLS9101 | HLS9102 | Water | NA | NA | 10" | 10" | Check Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23001 | 23.21 | 4171 | 2080_00006‐1
D | 01‐VHLS904 | LP HEAT EXCHANGER ISOLATION | HLS9171 | HLS9174 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 | 300 | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23005 | 23.21 | 4172 | 2080_00006‐1
D | 01‐VHLS905 | LP HEAT EXCHANGER ISOLATION | HLS9111 | HLS9179 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 490 | 41.4 | 254.7 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23004 | 23.21 | 4173 | 2080_00006‐1
D | 01‐VHLS907 | LP HEAT EXCHANGER ISOLATION | HLS9104 | HLS9105 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23004 | 23.21 | 4174 | 2080_00006‐1
D | 01‐VHLS908 | LP HEAT EXCHANGER ISOLATION | HLS9113 | HLS9123 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 490 | 41.4 | 254.7 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23004 | 23.21 | 4175 | 2080_00006‐1
D | 01‐VHLS909 | LP HEAT EXCHANGER BYPASS | HLS9114 | HLS9172 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 | 300 | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 3 | HP Valve | 2080_23034 | 23.21 | 4176 | 2080_00006‐1
D | 01‐VHBD904 | BLOW DOWN TANK CV ISOLATION | HBD9109 | HBD9109 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 1500 | 1500 | BW | BW |  | 78 | 5 | 9 | Bypass Equalizer Type 4 | HP Valve | 2080_23031 | 23.21 | 4177 | 2080_00007‐1
D | 01‐VHBD905 | BLOW DOWN TANK CV ISOLATION | HBD9110 | HBD9110 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 1500 | 1500 | BW | BW |  | 78 | 5 | 9 | Bypass Equalizer Type 4 | HP Valve | 2080_23031 | 23.21 | 4178 | 2080_00007‐1
D | 01‐VHBD906 | BLOW DOWN TANK CHECK | HBD9110 | HBD9110 | Water | NA | NA | 6" | 6" | Check Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 58 | 750 | 4 | 399 | 150 | 150 | BW | BW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23032 | 23.21 | 4179 | 2080_00007‐1
D | 01‐VHEH901 | EXHAUST SIDE INLET DUCT PRESSURE TRANSMITTER ISOLATION | HEH9801 | HEH9801 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1100 | 0.1 | 593.3 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4180 | 2080_00002‐1
D | 01‐VHEH902 | EXHAUST SIDE INLET DUCT PRESSURE TRANSMITTER ISOLATION | HEH9802 | HEH9802 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1100 | 0.1 | 593.3 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4181 | 2080_00002‐1
D | 01‐VHEH903 | EXHAUST SIDE INLET DUCT PRESSURE TRANSMITTER ISOLATION | HEH9803 | HEH9803 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1100 | 0.1 | 593.3 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4182 | 2080_00002‐1
D | 01‐VHEH904 | EXHAUST SIDE CO CATALYST 1 PRESSURE TRASMITTER ISOLATION | HEH9804 | HEH9804 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1033 | 0.1 | 556.1 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4183 | 2080_00002‐1
D | 01‐VHEH905 | EXHAUST SIDE CO CATALYST 1 PRESSURE TRASMITTER ISOLATION | HEH9805 | HEH9805 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1033 | 0.1 | 556.1 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4184 | 2080_00002‐1
D | 01‐VHEH906 | EXHAUST SIDE CO CATALYST 2 PRESSURE TRASMITTER ISOLATION | HEH9806 | HEH9806 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1 | 566 | 0.1 | 296.7 | 800 | 800 | SW | SW | SPARE 01‐VHIS954 on valve drawing 2080_23126 Rev D | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23126 | 23.22 | 4185 | 2080_00002‐1
D | 01‐VHEH907 | EXHAUST SIDE CO CATALYST 2 PRESSURE TRASMITTER ISOLATION | HEH9807 | HEH9807 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1 | 566 | 0.1 | 296.7 | 800 | 800 | SW | SW | SPARE 01‐VHIS955 on valve drawing 2080_23126 Rev D | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23126 | 23.22 | 4186 | 2080_00002‐1
D | 01‐VHEH908 | EXHAUST SIDE SCR CATALYST PRESSURE TRASMITTER ISOLATION | HEH9808 | HEH9808 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1 | 566 | 0.1 | 296.7 | 800 | 800 | SW | SW | SPARE 01‐VHIS956 on valve drawing 2080_23126 Rev D | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23126 | 23.22 | 4187 | 2080_00002‐1
D | 01‐VHEH909 | EXHAUST SIDE SCR CATALYST PRESSURE TRASMITTER ISOLATION | HEH9809 | HEH9809 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1 | 566 | 0.1 | 296.7 | 800 | 800 | SW | SW | SPARE 01‐VHIS957 on valve drawing 2080_23126 Rev D | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23126 | 23.22 | 4188 | 2080_00002‐1
D | 01‐VHEH912 | BURNER MAIN FUEL LINE DRAIN | BUR9901 | BUR9901 | Nat. Gas | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 100 | 130 | 6.9 | 54.4 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS985 on valve drawing 2080_23106 Rev D | N.A. | N.A. | ‐ |  | HP Valve | 2080_23106 | 23.22 | 4189 | 2080_00002‐1
D | 01‐VHEH913 | BURNER PILOT FUEL LINE DRAIN | BUR9902 | BUR9902 | Nat. Gas | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 100 | 130 | 6.9 | 54.4 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS986 on valve drawing 2080_23106 Rev D | N.A. | N.A. | ‐ |  | HP Valve | 2080_23106 | 23.22 | 4190 | 2080_00002‐1
D | 01‐VHEH914 | BURNER INSTRUMENT AIR DRAIN | BUR9903 | BUR9903 | Air | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 150 | 130 | 10.3 | 54.4 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS865 on valve drawing 2080_23106 Rev D | N.A. | N.A. | ‐ |  | HP Valve | 2080_23106 | 23.22 | 4191 | 2080_00002‐1
D | 01‐VHEH915 | BURNER COOLING AIR DRAIN | BUR9904 | BUR9904 | Air | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 20 | 110 | 1.4 | 43.3 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS907 on valve drawing 2080_23106 Rev D | N.A. | N.A. | ‐ |  | HP Valve | 2080_23106 | 23.22 | 4192 | 2080_00002‐1
D | 01‐VHLS805 | LP SATURATED STEAM VENT | HLS9992 | HLS9992 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4193 | 2080_00003‐1
D | 01‐VHLS806 | LP SATURATED STEAM VENT | HLS9992 | HLS9992 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4194 | 2080_00003‐1
D | 01‐VHLS831 | DEAERATOR VENT ISOLATION VALVE | HLS9975 | HLS9975 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | SPARE 01‐VHIS940 on valve drawing ("Spare 26" on 23E21 Rev C) | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4195 | 2080_00003‐1
D | 01‐VHLS832 | DEAERATOR VENT ISOLATION VALVE | HLS9977 | HLS9977 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | SPARE 01‐VHIS943 on valve drawing ("Spare 27" on 23E21 Rev C) | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4196 | 2080_00003‐1
D | 01‐VHLS833 | DEAERATOR VENT ISOLATION VALVE | HLS9975 | HLS9975 | Water | NA | NA | 2" | 2" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | New on Rev. D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23128 | 23.22 | 4197 | 2080_00003‐1
D | 01‐VHLS834 | DEAERATOR VENT ISOLATION VALVE | HLS9977 | HLS9977 | Water | NA | NA | 2" | 2" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | New on Rev. D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23128 | 23.22 | 4198 | 2080_00003‐1
D | 01‐VHLS923 | PREHEATER DRAIN | HLS9990 | HLS9990 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4199 | 2080_00003‐1
D | 01‐VHLS925 | PREHEATER DRAIN | HLS9990 | HLS9940 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4200 | 2080_00003‐1
D | 01‐VHLS926 | PREHEATER OUTLET PRESSURE INDICATOR ISOLATION | HLS9840 | HLS9840 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 2500 | 2500 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23109 | 23.22 | 4201 | 2080_00003‐1
D | 01‐VHLS927 | PREHEATER OUTLET PRESSURE INDICATOR ISOLATION | HLS9840 | HLS9840 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 2500 | 2500 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23109 | 23.22 | 4202 | 2080_00003‐1
D | 01‐VHLS930 | PREHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HLS9802 | HLS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4203 | 2080_00003‐1
D | 01‐VHLS931 | PREHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HLS9802 | HLS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4204 | 2080_00003‐1
D | 01‐VHLS932 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9803 | HLS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4205 | 2080_00003‐1
D | 01‐VHLS933 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9803 | HLS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4206 | 2080_00003‐1
D | 01‐VHLS934 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9804 | HLS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4207 | 2080_00003‐1
D | 01‐VHLS935 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9804 | HLS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4208 | 2080_00003‐1
D | 01‐VHLS936 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9805 | HLS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4209 | 2080_00003‐1
D | 01‐VHLS937 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9805 | HLS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4210 | 2080_00003‐1
D | 01‐VHLS938 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9806 | HLS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4211 | 2080_00003‐1
D | 01‐VHLS939 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9806 | HLS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4212 | 2080_00003‐1
D | 01‐VHLS942 | LP DRUM LCV BYPASS | HLS9128 | HLS9129 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 2 & 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4213 | 2080_00003‐1
D | 01‐VHLS943 | PREHEATER OUTLET DRAIN (DOWNSTREAM LCV) | HLS9916 | HLS9916 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23124 | 23.22 | 4214 | 2080_00003‐1
D | 01‐VHLS944 | PREHEATER OUTLET DRAIN (DOWNSTREAM LCV) | HLS9916 | HLS9917 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23124 | 23.22 | 4215 | 2080_00003‐1
D | 01‐VHLS945 | LP DRUM DEAERATOR PRESSURE INDICATOR ISOLATION | HLS9807 | HLS9807 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4216 | 2080_00003‐1
D | 01‐VHLS946 | LP DRUM DEAERATOR PRESSURE INDICATOR ISOLATION | HLS9807 | HLS9807 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4217 | 2080_00003‐1
D | 01‐VHLS947 | LP DRUM DEAERATOR VENT | HLS9975 | HLS9975 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4218 | 2080_00003‐1
D | 01‐VHLS948 | LP DRUM DEAERATOR VENT | HLS9977 | HLS9977 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4219 | 2080_00003‐1
D | 01‐VHLS949 | LP DRUM LEVEL GAUGE ISOLATION | HLS9814 | HLS9814 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4220 | 2080_00003‐1
D | 01‐VHLS950 | LP DRUM LEVEL INDICATION DRAIN | HLS9918 | HLS9918 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4221 | 2080_00003‐1
D | 01‐VHLS951 | LP DRUM LEVEL INDICATION DRAIN | HLS9919 | HLS9920 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4222 | 2080_00003‐1
D | 01‐VHLS952 | LP DRUM LEVEL INDICATION DRAIN | HLS9919 | HLS9919 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4223 | 2080_00003‐1
D | 01‐VHLS953 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9811 | HLS9811 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4224 | 2080_00003‐1
D | 01‐VHLS954 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9811 | HLS9811 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4225 | 2080_00003‐1
D | 01‐VHLS955 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9813 | HLS9813 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4226 | 2080_00003‐1
D | 01‐VHLS956 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9813 | HLS9813 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4227 | 2080_00003‐1
D | 01‐VHLS957 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9808 | HLS9808 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4228 | 2080_00003‐1
D | 01‐VHLS958 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9808 | HLS9808 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4229 | 2080_00003‐1
D | 01‐VHLS959 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9810 | HLS9810 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4230 | 2080_00003‐1
D | 01‐VHLS960 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9810 | HLS9810 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4231 | 2080_00003‐1
D | 01‐VHLS961 | LP DRUM LEVEL GAUGE ISOLATION | HLS9814 | HLS9815 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4232 | 2080_00003‐1
D | 01‐VHLS962 | LP DRUM LEVEL GAUGE ISOLATION | HLS9816 | HLS9817 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4233 | 2080_00003‐1
D | 01‐VHLS963 | LP DRUM LEVEL GAUGE ISOLATION | HLS9816 | HLS9816 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4234 | 2080_00003‐1
D | 01‐VHLS964 | LP DRUM LEVEL GAUGE ISOLATION | HLS9821 | HLS9821 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4235 | 2080_00003‐1
D | 01‐VHLS965 | LP DRUM LEVEL GAUGE ISOLATION | HLS9821 | HLS9822 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4236 | 2080_00003‐1
D | 01‐VHLS966 | LP DRUM LEVEL INDICATION DRAIN | HLS9925 | HLS9926 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4237 | 2080_00003‐1
D | 01‐VHLS967 | LP DRUM LEVEL INDICATION DRAIN | HLS9925 | HLS9925 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4238 | 2080_00003‐1
D | 01‐VHLS968 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9820 | HLS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4239 | 2080_00003‐1
D | 01‐VHLS969 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9820 | HLS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4240 | 2080_00003‐1
D | 01‐VHLS970 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9818 | HLS9818 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4241 | 2080_00003‐1
D | 01‐VHLS971 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9818 | HLS9818 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4242 | 2080_00003‐1
D | 01‐VHLS972 | LP DRUM LEVEL GAUGE ISOLATION | HLS9823 | HLS9824 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4243 | 2080_00003‐1
D | 01‐VHLS973 | LP DRUM LEVEL GAUGE ISOLATION | HLS9823 | HLS9823 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4244 | 2080_00003‐1
D | 01‐VHLS974 | LP DRUM NITROGEN ISOLATION | HRG9105 | HLS9404 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4245 | 2080_00003‐1
D | 01‐VHLS975 | LP DRUM NITROGEN SUPPLY NRV | HLS9404 | HLS9404 | Water/Steam | NA | NA | 2" | 2" | Stop Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 1500 | 1500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23102 | 23.22 | 4246 | 2080_00003‐1
D | 01‐VHLS976 | LP DRUM PRESSURE INDICATOR ISOLATION | HLS9825 | HLS9825 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4247 | 2080_00003‐1
D | 01‐VHLS977 | LP DRUM PRESSURE INDICATOR ISOLATION | HLS9825 | HLS9825 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4248 | 2080_00003‐1
D | 01‐VHLS978 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9826 | HLS9826 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4249 | 2080_00003‐1
D | 01‐VHLS979 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9826 | HLS9826 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4250 | 2080_00003‐1
D | 01‐VHLS980 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9827 | HLS9827 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4251 | 2080_00003‐1
D | 01‐VHLS981 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9827 | HLS9827 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4252 | 2080_00003‐1
D | 01‐VHLS982 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9828 | HLS9828 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4253 | 2080_00003‐1
D | 01‐VHLS983 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9828 | HLS9828 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4254 | 2080_00003‐1
D | 01‐VHLS985 | LP SPARGING STEAM DRAIN | HLS9923 | HLS9923 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 425 | 454 | 29.3 | 234.4 | 2500 | 2500 | SW | SW | SPARE_297 on valve drawing 2080_23113 Rev D | 638 | 44 | 8 | ‐ | HP Valve | 2080_23113 | 23.22 | 4255 | 2080_00003‐1
D | 01‐VHLS988 | LP ECONOMIZER OUTLET VENT | HLS9976 | HLS9976 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | SPARE 01‐VHIS993 on valve drawing 2080_23120 Rev D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4256 | 2080_00003‐1
D | 01‐VHLS989 | LP ECONOMIZER OUTLET VENT | HLS9976 | HLS9976 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | SPARE 01‐VHIS936 on valve drawing 2080_23120 Rev D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4257 | 2080_00003‐1
D | 01‐VHLS990 | LP DRUM WATER SAMPLE ISOLATION | HLS9606 | HLS9606 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 162 | 372 | 11.2 | 188.7 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4258 | 2080_00003‐1
D | 01‐VHLS991 | LP DRUM WATER SAMPLE ISOLATION | HLS9606 | HLS9606 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 162 | 372 | 11.2 | 188.7 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4259 | 2080_00003‐1
D | 01‐VHLS992 | LP SPARGING STEAM STRAIN DRAIN | HLS9921 | HLS9921 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 162 | 372 | 11.2 | 188.7 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23113 | 23.22 | 4260 | 2080_00003‐1
D | 01‐VHLS993 | LP SPARGING STEAM STRAIN DRAIN | HLS9921 | HLS9922 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 162 | 372 | 11.2 | 188.7 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23113 | 23.22 | 4261 | 2080_00003‐1
D | 01‐VHLS997 | PREHEATER OUTLET DRAIN | HLS9301 | HLS9301 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4262 | 2080_00003‐1
D | 01‐VHLS998 | PREHEATER OUTLET DRAIN | HLS9301 | HLS9302 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4263 | 2080_00003‐1
D | 01‐VHLS999 | LP SPARGING STEAM DRAIN | HLS9923 | HLS9924 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 425 | 454 | 29.3 | 234.4 | 2500 | 2500 | SW | SW | SPARE_428 on valve drawing 2080_23113 Rev D | 638 | 44 | 8 | ‐ | HP Valve | 2080_23113 | 23.22 | 4264 | 2080_00003‐1
D | 01‐VHLS808 | LP SUPERHEATED STEAM SAMPLE ISOLATION | HLS8610 | HLS8610 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 131 | 623 | 9 | 328.5 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23108 | 23.22 | 4265 | 2080_00003‐2
D | 01‐VHLS809 | LP SUPERHEATED STEAM SAMPLE ISOLATION | HLS8610 | HLS8610 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 131 | 623 | 9 | 328.5 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23108 | 23.22 | 4266 | 2080_00003‐2
D | 01‐VHLS811 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9841 | HLS9841 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4267 | 2080_00003‐2
D | 01‐VHLS812 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9841 | HLS9841 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4268 | 2080_00003‐2
D | 01‐VHLS813 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9842 | HLS9842 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4269 | 2080_00003‐2
D | 01‐VHLS814 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9842 | HLS9842 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4270 | 2080_00003‐2
D | 01‐VHLS815 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9843 | HLS9843 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4271 | 2080_00003‐2
D | 01‐VHLS816 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9843 | HLS9843 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4272 | 2080_00003‐2
D | 01‐VHLS817 | LP SUPERHEATED STEAM PRESSURE INDICATOR ISOLATION | HLS9844 | HLS9844 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4273 | 2080_00003‐2
D | 01‐VHLS818 | LP SUPERHEATED STEAM PRESSURE INDICATOR ISOLATION | HLS9844 | HLS9844 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4274 | 2080_00003‐2
D | 01‐VHLS819 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8809 | HLS8809 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4275 | 2080_00003‐2
D | 01‐VHLS820 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8809 | HLS8809 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4276 | 2080_00003‐2
D | 01‐VHLS821 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8807 | HLS8807 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4277 | 2080_00003‐2
D | 01‐VHLS822 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8807 | HLS8807 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4278 | 2080_00003‐2
D | 01‐VHLS825 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8805 | HLS8805 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23109 | 23.22 | 4279 | 2080_00003‐2
D | 01‐VHLS826 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8805 | HLS8805 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23109 | 23.22 | 4280 | 2080_00003‐2
D | 01‐VHLS827 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8803 | HLS8803 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW | 01‐VHEH906 on valve drawing 2080_23127 Rev B | 196 | 14 | 2 | ‐ | HP Valve | 2080_23127 | 23.22 | 4281 | 2080_00003‐2
D | 01‐VHLS828 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8803 | HLS8803 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW | 01‐VHEH908 on valve drawing 2080_23127 Rev B | 196 | 14 | 2 | ‐ | HP Valve | 2080_23127 | 23.22 | 4282 | 2080_00003‐2
D | 01‐VHLS986 | LP SUPERHEATER OUTLET DRAIN POT CLEANOUT DRAIN | HLS9303 | HLS9303 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 624 | 9 | 328.7 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23126 | 23.22 | 4283 | 2080_00003‐2
D | 01‐VHLS987 | LP SUPERHEATER OUTLET DRAIN POT CLEANOUT DRAIN | HLS9303 | HLS9304 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 624 | 9 | 328.7 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23126 | 23.22 | 4284 | 2080_00003‐2
D | 01‐VHIS904 | IP FEEDWATER BOILER FILL ISOLATION | HIS9108 | HIS9134 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4285 | 2080_00004‐1
D | 01‐VHIS905 | IP FEEDWATER BOILER FILL CHECK VALVE | HIS9134 | HIS9109 | Water | NA | NA | 2" | 2" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23128 | 23.22 | 4286 | 2080_00004‐1
D | 01‐VHIS906 | IP FEEDWATER PRESSURE TRANSMITTER ISOLATION | HIS9801 | HIS9801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4287 | 2080_00004‐1
D | 01‐VHIS907 | IP FEEDWATER PRESSURE TRANSMITTER ISOLATION | HIS9801 | HIS9801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4288 | 2080_00004‐1
D | 01‐VHIS910 | IP ECONOMIZER INLET DRAIN | HIS9903 | HIS9903 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4289 | 2080_00004‐1
D | 01‐VHIS911 | IP ECONOMIZER DRAIN | HIS9904 | HIS9308 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.6 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4290 | 2080_00004‐1
D | 01‐VHIS912 | IP ECONOMIZER DRAIN | HIS9905 | HIS9309 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4291 | 2080_00004‐1
D | 01‐VHIS913 | IP ECONOMIZER DRAIN | HIS9309 | HIS9906 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 9 & 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4292 | 2080_00004‐1
D | 01‐VHIS915 | IP ECONOMIZER VENT | HIS9952 | HIS9353 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.6 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4293 | 2080_00004‐1
D | 01‐VHIS917 | IP ECONOMIZER VENT | HIS9954 | HIS9358 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4294 | 2080_00004‐1
D | 01‐VHIS918 | IP ECONOMIZER VENT | HIS9978 | HIS9978 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4295 | 2080_00004‐1
D | 01‐VHIS919 | IP FEEDWATER DRAIN | HIS9901 | HIS9901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4296 | 2080_00004‐1
D | 01‐VHIS920 | IP FEEDWATER DRAIN | HIS9901 | HIS9902 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4297 | 2080_00004‐1
D | 01‐VHIS846 | IP SATURATED STEAM VENT | HIS9957 | HIS9957 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23106 | 23.22 | 4298 | 2080_00004‐2
D | 01‐VHIS847 | IP SATURATED STEAM VENT | HIS9957 | HIS9957 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23106 | 23.22 | 4299 | 2080_00004‐2
D | 01‐VHIS848 | IP SATURATED STEAM VENT | HIS9958 | HIS9958 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23106 | 23.22 | 4300 | 2080_00004‐2
D | 01‐VHIS849 | IP SATURATED STEAM VENT | HIS9958 | HIS9958 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23106 | 23.22 | 4301 | 2080_00004‐2
D | 01‐VHIS850 | IP SATURATED STEAM VENT | HIS9959 | HIS9959 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23120 | 23.22 | 4302 | 2080_00004‐2
D | 01‐VHIS851 | IP SATURATED STEAM VENT | HIS9959 | HIS9959 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23120 | 23.22 | 4303 | 2080_00004‐2
D | 01‐VHIS852 | IP SPARGING STEAM STRAIN DRAIN | HIS8306 | HIS8306 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 656 | 498 | 45.2 | 259 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23113 | 23.22 | 4304 | 2080_00004‐2
D | 01‐VHIS853 | IP SPARGING STEAM STRAIN DRAIN | HIS8306 | HIS8307 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 656 | 498 | 45.2 | 259 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23113 | 23.22 | 4305 | 2080_00004‐2
D | 01‐VHIS854 | IP ECONOMIZER OUTLET DRAIN | HIS8310 | HIS8310 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4306 | 2080_00004‐2
D | 01‐VHIS855 | IP ECONOMIZER OUTLET DRAIN | HIS8310 | HIS8311 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4307 | 2080_00004‐2
D | 01‐VHIS860 | IP SPARGING STEAM DRAIN | HIS8308 | HIS8308 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 656 | 498 | 45.2 | 259 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS963 on valve drawing 2080_23113 Rev D | 935 | 65 | 4 | ‐ | HP Valve | 2080_23113 | 23.22 | 4308 | 2080_00004‐2
D | 01‐VHIS861 | IP SPARGING STEAM DRAIN | HIS8308 | HIS8309 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 656 | 498 | 45.2 | 259 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS964 on valve drawing 2080_23113 Rev D | 935 | 65 | 4 | ‐ | HP Valve | 2080_23113 | 23.22 | 4309 | 2080_00004‐2
D | 01‐VHIS914 | IP FEEDWATER PRESSURE INDICATOR ISOLATION | HIS9853 | HIS9853 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 2500 | 2500 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4310 | 2080_00004‐2
D | 01‐VHIS916 | IP FEEDWATER PRESSURE INDICATOR ISOLATION | HIS9853 | HIS9853 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 2500 | 2500 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4311 | 2080_00004‐2
D | 01‐VHIS922 | IP ECONOMIZER OUTLET PRESSURE TRANSMITTER ISOLATION | HIS9802 | HIS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4312 | 2080_00004‐2
D | 01‐VHIS923 | IP ECONOMIZER OUTLET PRESSURE TRANSMITTER ISOLATION | HIS9802 | HIS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4313 | 2080_00004‐2
D | 01‐VHIS924 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9803 | HIS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4314 | 2080_00004‐2
D | 01‐VHIS925 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9803 | HIS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4315 | 2080_00004‐2
D | 01‐VHIS926 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9804 | HIS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4316 | 2080_00004‐2
D | 01‐VHIS927 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9804 | HIS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4317 | 2080_00004‐2
D | 01‐VHIS928 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9805 | HIS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4318 | 2080_00004‐2
D | 01‐VHIS929 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9805 | HIS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4319 | 2080_00004‐2
D | 01‐VHIS930 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9806 | HIS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4320 | 2080_00004‐2
D | 01‐VHIS931 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9806 | HIS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4321 | 2080_00004‐2
D | 01‐VHIS932 | IP ECONOMIZER OUTLET DRAIN | HIS9908 | HIS9908 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4322 | 2080_00004‐2
D | 01‐VHIS933 | IP ECONOMIZER OUTLET DRAIN | HIS9908 | HIS9909 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4323 | 2080_00004‐2
D | 01‐VHIS936 | IP DRUM LCV BYPASS | HIS9118 | HIS9119 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 4 & 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4324 | 2080_00004‐2
D | 01‐VHIS937 | IP ECONOMIZER OUTLET DRAIN (DOWNSTREAM LCV) | HIS9910 | HIS9910 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23124 | 23.22 | 4325 | 2080_00004‐2
D | 01‐VHIS938 | IP ECONOMIZER OUTLET DRAIN (DOWNSTREAM LCV) | HIS9910 | HIS9911 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23124 | 23.22 | 4326 | 2080_00004‐2
D | 01‐VHIS939 | IP DRUM LEVEL GAUGE ISOLATION | HIS9807 | HIS9807 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4327 | 2080_00004‐2
D | 01‐VHIS940 | IP DRUM LEVEL GAUGE ISOLATION | HIS9807 | HIS9807 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4328 | 2080_00004‐2
D | 01‐VHIS941 | IP DRUM LEVEL GAUGE DRAIN | HIS9907 | HIS9920 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4329 | 2080_00004‐2
D | 01‐VHIS942 | IP DRUM LEVEL GAUGE DRAIN | HIS9907 | HIS9907 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4330 | 2080_00004‐2
D | 01‐VHIS943 | IP DRUM LEVEL GAUGE ISOLATION | HIS9810 | HIS9810 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4331 | 2080_00004‐2
D | 01‐VHIS944 | IP DRUM LEVEL GAUGE DRAIN | HIS9919 | HIS9919 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4332 | 2080_00004‐2
D | 01‐VHIS945 | IP DRUM LEVEL GAUGE DRAIN | HIS9918 | HIS9928 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4333 | 2080_00004‐2
D | 01‐VHIS946 | IP DRUM LEVEL GAUGE DRAIN | HIS9918 | HIS9918 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4334 | 2080_00004‐2
D | 01‐VHIS947 | IP DRUM LEVEL GAUGE ISOLATION | HIS9812 | HIS9813 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4335 | 2080_00004‐2
D | 01‐VHIS948 | IP DRUM LEVEL GAUGE ISOLATION | HIS9810 | HIS9811 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4336 | 2080_00004‐2
D | 01‐VHIS949 | IP DRUM LEVEL GAUGE ISOLATION | HIS9812 | HIS9812 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4337 | 2080_00004‐2
D | 01‐VHIS950 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9814 | HIS9814 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4338 | 2080_00004‐2
D | 01‐VHIS951 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9814 | HIS9814 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4339 | 2080_00004‐2
D | 01‐VHIS952 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9816 | HIS9816 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4340 | 2080_00004‐2
D | 01‐VHIS953 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9816 | HIS9816 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4341 | 2080_00004‐2
D | 01‐VHIS954 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9817 | HIS9817 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4342 | 2080_00004‐2
D | 01‐VHIS955 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9817 | HIS9817 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4343 | 2080_00004‐2
D | 01‐VHIS956 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9819 | HIS9819 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4344 | 2080_00004‐2
D | 01‐VHIS957 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9819 | HIS9819 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4345 | 2080_00004‐2
D | 01‐VHIS958 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9820 | HIS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4346 | 2080_00004‐2
D | 01‐VHIS959 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9820 | HIS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4347 | 2080_00004‐2
D | 01‐VHIS960 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9822 | HIS9822 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4348 | 2080_00004‐2
D | 01‐VHIS961 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9822 | HIS9822 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4349 | 2080_00004‐2
D | 01‐VHIS963 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9823 | HIS9823 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4350 | 2080_00004‐2
D | 01‐VHIS964 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9823 | HIS9823 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4351 | 2080_00004‐2
D | 01‐VHIS965 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9824 | HIS9824 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4352 | 2080_00004‐2
D | 01‐VHIS966 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9824 | HIS9824 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4353 | 2080_00004‐2
D | 01‐VHIS967 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9825 | HIS9825 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4354 | 2080_00004‐2
D | 01‐VHIS968 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9825 | HIS9825 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4355 | 2080_00004‐2
D | 01‐VHIS969 | IP DRUM PRESSURE INDICATOR ISOLATION | HIS9826 | HIS9826 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4356 | 2080_00004‐2
D | 01‐VHIS970 | IP DRUM PRESSURE INDICATOR ISOLATION | HIS9826 | HIS9826 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4357 | 2080_00004‐2
D | 01‐VHIS971 | IP DRUM NITROGEN SUPPLY ISOLATION | HRG9104 | HIS9404 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4358 | 2080_00004‐2
D | 01‐VHIS972 | IP DRUM NITROGEN SUPPLY NRV | HIS9404 | HIS9404 | Water/Steam | NA | NA | 2" | 2" | Stop Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 1500 | 1500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23102 | 23.22 | 4359 | 2080_00004‐2
D | 01‐VHIS973 | IP DRUM WATER SAMPLE ISOLATION | HIS9602 | HIS9602 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4360 | 2080_00004‐2
D | 01‐VHIS974 | IP DRUM WATER SAMPLE ISOLATION | HIS9602 | HIS9602 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4361 | 2080_00004‐2
D | 01‐VHIS976 | IP SATURATED STEAM VENT | HIS9960 | HIS9960 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23120 | 23.22 | 4362 | 2080_00004‐2
D | 01‐VHIS977 | IP SATURATED STEAM VENT | HIS9960 | HIS9960 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23120 | 23.22 | 4363 | 2080_00004‐2
D | 01‐VHIS979 | IP DRUM LEVEL GAUGE ISOLATION | HIS9809 | HIS9809 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4364 | 2080_00004‐2
D | 01‐VHIS991 | IP DRUM INLET CHEMICAL INJECTION CHECK VALVE | HIS9504 | HIS9504 | Water | NA | NA | 1" | 1" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23129 | 23.22 | 4365 | 2080_00004‐2
D | 01‐VHIS992 | IP DRUM INLET CHEMICAL INJECTION ISOLATION | HIS9504 | HIS9504 | Water | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23121 | 23.22 | 4366 | 2080_00004‐2
D | 01‐VHIS993 | IP DRUM LEVEL GAUGE ISOLATION | HIS9809 | HIS9809 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4367 | 2080_00004‐2
D | 01‐VHIS998 | IP TO LP PEGGING STEAM VENT | HIS9979 | HIS9979 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 365 | 9 | 184.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4368 | 2080_00004‐2
D | 01‐VHIS999 | IP TO LP PEGGING STEAM VENT | HIS9979 | HIS9979 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 365 | 9 | 184.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4369 | 2080_00004‐2
D | 01‐VHIS801 | IP SUPERHEATED STEAM DRAIN | HIS9930 | HIS9930 | Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4370 | 2080_00004‐3
D | 01‐VHIS802 | IP SUPERHEATED STEAM DRAIN | HIS9930 | HIS9930 | Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4371 | 2080_00004‐3
D | 01‐VHIS856 | IP SUPERHEATER OUTLET DRAIN POT CLEANOUT DRAIN | HIS8313 | HIS8313 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23126 | 23.22 | 4372 | 2080_00004‐3
D | 01‐VHIS857 | IP SUPERHEATER OUTLET DRAIN POT CLEANOUT DRAIN | HIS8313 | HIS8314 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23126 | 23.22 | 4373 | 2080_00004‐3
D | 01‐VHIS858 | IP STEAM OUTLET DRAIN POT CLEANOUT DRAIN | HIS8312 | HIS8312 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23126 | 23.22 | 4374 | 2080_00004‐3
D | 01‐VHIS859 | IP STEAM OUTLET DRAIN POT CLEANOUT DRAIN | HIS8312 | HIS8315 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23126 | 23.22 | 4375 | 2080_00004‐3
D | 01‐VHIS864 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9838 | HIS9838 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4376 | 2080_00004‐3
D | 01‐VHIS865 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9838 | HIS9838 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4377 | 2080_00004‐3
D | 01‐VHIS866 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9836 | HIS9836 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4378 | 2080_00004‐3
D | 01‐VHIS867 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9836 | HIS9836 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4379 | 2080_00004‐3
D | 01‐VHIS982 | IP SUPERHEATED STEAM SAMPLE ISOLATION | HIS9609 | HIS9609 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 624 | 622 | 43 | 327.6 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23108 | 23.22 | 4380 | 2080_00004‐3
D | 01‐VHIS983 | IP SUPERHEATED STEAM SAMPLE ISOLATION | HIS9609 | HIS9609 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 624 | 622 | 43 | 327.6 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23108 | 23.22 | 4381 | 2080_00004‐3
D | 01‐VHIS985 | IP SUPERHEATED STEAM PRESSURE INDICATION ISOLATION | HIS9827 | HIS9827 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4382 | 2080_00004‐3
D | 01‐VHIS986 | IP SUPERHEATED STEAM PRESSURE INDICATION ISOLATION | HIS9827 | HIS9827 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4383 | 2080_00004‐3
D | 01‐VHIS987 | IP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HIS9828 | HIS9828 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4384 | 2080_00004‐3
D | 01‐VHIS988 | IP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HIS9828 | HIS9828 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4385 | 2080_00004‐3
D | 01‐VHIS994 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9834 | HIS9834 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4386 | 2080_00004‐3
D | 01‐VHIS995 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9834 | HIS9834 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4387 | 2080_00004‐3
D | 01‐VHIS996 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9836 | HIS9836 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4388 | 2080_00004‐3
D | 01‐VHIS997 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9836 | HIS9836 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4389 | 2080_00004‐3
D | 01‐VHRS803 | COLD REHEAT RETURN PRESSURE TRANSMITTER ISOLATION | HRS8837 | HRS8837 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 783 | 43 | 417.2 | 800 | 800 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23122 | 23.22 | 4390 | 2080_00004‐4
D | 01‐VHRS804 | COLD REHEAT RETURN PRESSURE TRANSMITTER ISOLATION | HRS8837 | HRS8837 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 783 | 43 | 417.2 | 800 | 800 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23122 | 23.22 | 4391 | 2080_00004‐4
D | 01‐VHRS805 | COLD REHEAT RETURN PRESSURE INDICATOR ISOLATION | HRS8838 | HRS8838 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 783 | 43 | 417.2 | 800 | 800 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23122 | 23.22 | 4392 | 2080_00004‐4
D | 01‐VHRS806 | COLD REHEAT RETURN PRESSURE INDICATOR ISOLATION | HRS8838 | HRS8838 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 783 | 43 | 417.2 | 800 | 800 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23122 | 23.22 | 4393 | 2080_00004‐4
D | 01‐VHRS807 | REHEATER INLET VENT | HRS9988 | HRS9988 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F22 | 624 | 752 | 43 | 400.2 | 900 | 900 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23132 | 23.22 | 4394 | 2080_00004‐4
D | 01‐VHRS808 | REHEATER INLET VENT | HRS9988 | HRS9988 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F22 | 624 | 752 | 43 | 400.2 | 900 | 900 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23132 | 23.22 | 4395 | 2080_00004‐4
D | 01‐VHRS809 | REHEATER INLET NITROGEN FILL ISOLATION | HRG9102 | HRS9402 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F22 | 624 | 752 | 43 | 400.2 | 2500 | 2500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23105 | 23.22 | 4396 | 2080_00004‐4
D | 01‐VHRS810 | REHEATER INLET NITROGEN FILL CHECK VALVE | HRS9402 | HRS9402 | Steam | NA | NA | 2" | 2" | Check Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F22 | 624 | 752 | 43 | 400.2 | 2500 | 2500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23130 | 23.22 | 4397 | 2080_00004‐4
D | 01‐VHRS813 | HOT REHEAT OUTLET PRESSURE TRANSMITTER ISOLATION | HRS9803 | HRS9803 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 LTD | 2500 LTD | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23110 | 23.22 | 4398 | 2080_00004‐4
D | 01‐VHRS814 | HOT REHEAT OUTLET PRESSURE TRANSMITTER ISOLATION | HRS9803 | HRS9803 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 LTD | 2500 LTD | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23110 | 23.22 | 4399 | 2080_00004‐4
D | 01‐VHRS820 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9805 | HRS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS920 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4400 | 2080_00004‐4
D | 01‐VHRS821 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9805 | HRS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS921 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4401 | 2080_00004‐4
D | 01‐VHRS822 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9806 | HRS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS922 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4402 | 2080_00004‐4
D | 01‐VHRS823 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9806 | HRS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS923 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4403 | 2080_00004‐4
D | 01‐VHRS824 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9807 | HRS9807 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS924 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4404 | 2080_00004‐4
D | 01‐VHRS825 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9807 | HRS9807 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS925 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4405 | 2080_00004‐4
D | 01‐VHRS826 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HRS9808 | HRS9808 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS926 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4406 | 2080_00004‐4
D | 01‐VHRS827 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HRS9808 | HRS9808 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS927 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4407 | 2080_00004‐4
D | 01‐VHRS828 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HRS9809 | HRS9809 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | SPARE_446 on valve drawing 2080_23109 Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4408 | 2080_00004‐4
D | 01‐VHRS829 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HRS9809 | HRS9809 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | SPARE_447 on valve drawing 2080_23109 Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4409 | 2080_00004‐4
D | 01‐VHRS832 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9810 | HRS9810 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS932 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4410 | 2080_00004‐4
D | 01‐VHRS833 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9810 | HRS9810 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS933 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4411 | 2080_00004‐4
D | 01‐VHRS834 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9811 | HRS9811 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS934 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4412 | 2080_00004‐4
D | 01‐VHRS835 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9811 | HRS9811 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS935 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4413 | 2080_00004‐4
D | 01‐VHRS836 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9812 | HRS9812 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS936 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4414 | 2080_00004‐4
D | 01‐VHRS837 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9812 | HRS9812 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS937 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4415 | 2080_00004‐4
D | 01‐VHRS838 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9813 | HRS9813 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS938 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4416 | 2080_00004‐4
D | 01‐VHRS839 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9813 | HRS9813 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS939 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4417 | 2080_00004‐4
D | 01‐VHRS848 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER STRAINER DRAIN | HRS9304 | HRS9304 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS‐948 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4418 | 2080_00004‐4
D | 01‐VHRS849 | REHEAT INTERSTAGE ATTEMPERATOR STRAINER COOLING WATER DRAIN | HRS9304 | HRS9305 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS‐949 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4419 | 2080_00004‐4
D | 01‐VHRS860 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DRAIN | HRS9302 | HRS9302 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS‐960 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4420 | 2080_00004‐4
D | 01‐VHRS861 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DRAIN | HRS9302 | HRS9303 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS‐961 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4421 | 2080_00004‐4
D | 01‐VHRS862 | REHEAT INTERSTAGE ATTEMPERATOR DRAIN | HRS9306 | HRS9306 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 946 | 43 | 508 | 900 | 900 | SW | SW | Previously 01‐VHRS‐962 on P&ID Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23111 | 23.22 | 4422 | 2080_00004‐4
D | 01‐VHRS863 | REHEAT INTERSTAGE ATTEMPERATOR DRAIN | HRS9306 | HRS9307 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 946 | 43 | 508 | 900 | 900 | SW | SW | Previously 01‐VHRS‐963 on P&ID Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23111 | 23.22 | 4423 | 2080_00004‐4
D | 01‐VHRS901 | HOT REHEAT STEAM SAMPLE ISOLATION | HRS9601 | HRS9601 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 624 | 1096 | 43 | 591.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23108 | 23.22 | 4424 | 2080_00004‐4
D | 01‐VHRS902 | HOT REHEAT STEAM SAMPLE ISOLATION | HRS9601 | HRS9601 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 624 | 1096 | 43 | 591.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23108 | 23.22 | 4425 | 2080_00004‐4
D | 01‐VHRS903 | HOT REHEAT OUTLET PRESSURE TRANSMITTER ISOLATION | HRS9801 | HRS9801 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 LTD | 2500 LTD | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23110 | 23.22 | 4426 | 2080_00004‐4
D | 01‐VHRS904 | HOT REHEAT OUTLET PRESSURE TRANSMITTER ISOLATION | HRS9801 | HRS9801 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 LTD | 2500 LTD | SW | SW | SPARE_427 on valve drawing 2080_23110 Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23110 | 23.22 | 4427 | 2080_00004‐4
D | 01‐VHRS911 | HOT REHEAT OUTLET PRESSURE INDICATOR ISOLATION | HRS9802 | HRS9802 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 900 | 900 | SW | SW | Previously 01‐VHRS905 on P&ID Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23112 | 23.22 | 4428 | 2080_00004‐4
D | 01‐VHRS912 | HOT REHEAT OUTLET PRESSURE INDICATOR ISOLATION | HRS9802 | HRS9802 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 900 | 900 | SW | SW | Previously 01‐VHRS906 on P&ID Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23112 | 23.22 | 4429 | 2080_00004‐4
D | 01‐VHRS918 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9804 | HRS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4430 | 2080_00004‐4
D | 01‐VHRS919 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9804 | HRS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4431 | 2080_00004‐4
D | 01‐VHRS969 | REHEATER INTERSTAGE ATTEMPERATOR DRAIN POT CLEANOUT DRAIN | HRS9308 | HRS9308 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 624 | 946 | 43 | 508 | 1500 | 1500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23116 | 23.22 | 4432 | 2080_00004‐4
D | 01‐VHRS970 | REHEATER INTERSTAGE ATTEMPERATOR DRAIN POT CLEANOUT DRAIN | HRS9308 | HRS9308 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 624 | 946 | 43 | 508 | 1500 | 1500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23116 | 23.22 | 4433 | 2080_00004‐4
D | 01‐VHHS854 | HP ECONOMIZER INLET PRESSURE INDICATOR ISOLATION | HHS8806 | HHS8806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4434 | 2080_00005‐1
D | 01‐VHHS855 | HP ECONOMIZER INLET PRESSURE INDICATOR ISOLATION | HHS8806 | HHS8806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4435 | 2080_00005‐1
D | 01‐VHHS856 | HP FEEDWATER INLET DRAIN | HHS9901 | HHS9901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 4436 | 2080_00005‐1
D | 01‐VHHS857 | HP FEEDWATER INLET DRAIN | HHS9901 | HHS9902 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 4437 | 2080_00005‐1
D | 01‐VHHS858 | HP FEEDWATER INLET DRAIN | HHS9903 | HHS9903 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 4438 | 2080_00005‐1
D | 01‐VHHS859 | HP FEEDWATER INLET DRAIN | HHS9903 | HHS9904 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 4439 | 2080_00005‐1
D | 01‐VHHS900 | HP ECONOMIZER DRAIN | HHS9909 | HHS9317 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4440 | 2080_00005‐1
D | 01‐VHHS905 | HP ECONOMIZER DRAIN | HHS9932 | HHS9933 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4441 | 2080_00005‐1
D | 01‐VHHS906 | HP ECONOMIZER DRAIN | HHS9917 | HHS9946 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4442 | 2080_00005‐1
D | 01‐VHHS907 | HP DRUM LCV BYPASS | HHS9247 | HHS9248 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 4443 | 2080_00005‐1
D | 01‐VHHS912 | HP FEEDWATER INLET DRAIN | HHS9905 | HHS9905 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 4444 | 2080_00005‐1
D | 01‐VHHS913 | HP FEEDWATER INLET DRAIN | HHS9905 | HHS9906 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 4445 | 2080_00005‐1
D | 01‐VHHS914 | HP ECONOMIZER INLET PRESSURE TRANSMITTER ISOLATION | HHS9806 | HHS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4446 | 2080_00005‐1
D | 01‐VHHS915 | HP ECONOMIZER INLET PRESSURE TRANSMITTER ISOLATION | HHS9806 | HHS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4447 | 2080_00005‐1
D | 01‐VHHS916 | HP FEEDWATER INLET PRESSURE TRANSMITTER ISOLATION | HHS9801 | HHS9801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4448 | 2080_00005‐1
D | 01‐VHHS917 | HP FEEDWATER INLET PRESSURE TRANSMITTER ISOLATION | HHS9801 | HHS9801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4449 | 2080_00005‐1
D | 01‐VHHS918 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9802 | HHS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4450 | 2080_00005‐1
D | 01‐VHHS919 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9802 | HHS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4451 | 2080_00005‐1
D | 01‐VHHS920 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9803 | HHS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4452 | 2080_00005‐1
D | 01‐VHHS921 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9803 | HHS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4453 | 2080_00005‐1
D | 01‐VHHS922 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9804 | HHS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4454 | 2080_00005‐1
D | 01‐VHHS923 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9804 | HHS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4455 | 2080_00005‐1
D | 01‐VHHS924 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9805 | HHS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4456 | 2080_00005‐1
D | 01‐VHHS925 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9805 | HHS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4457 | 2080_00005‐1
D | 01‐VHHS926 | HP BOILER FILL ISOLATION | HHS9121 | HHS9122 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4458 | 2080_00005‐1
D | 01‐VHHS927 | HP BOILER FILL CHECK VALVE | HHS9122 | HHS9122 | Water | NA | NA | 2" | 2" | Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23118 | 23.22 | 4459 | 2080_00005‐1
D | 01‐VHHS928 | HP BOILER FILL ISOLATION | HHS9122 | HHS9123 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4460 | 2080_00005‐1
D | 01‐VHHS929 | HP ECONOMIZER DRAIN | HHS9313 | HHS9314 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4461 | 2080_00005‐1
D | 01‐VHHS930 | HP ECONOMIZER DRAIN | HHS9910 | HHS9912 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4462 | 2080_00005‐1
D | 01‐VHHS931 | HP ECONOMIZER DRAIN | HHS9913 | HHS9915 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4463 | 2080_00005‐1
D | 01‐VHHS932 | HP ECONOMIZER DRAIN | HHS9916 | HHS9917 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4464 | 2080_00005‐1
D | 01‐VHHS933 | HP ECONOMIZER DRAIN | HHS9918 | HHS9920 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4465 | 2080_00005‐1
D | 01‐VHHS934 | HP ECONOMIZER DRAIN | HHS9921 | HHS9923 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4466 | 2080_00005‐1
D | 01‐VHHS935 | HP ECONOMIZER DRAIN | HHS9924 | HHS9926 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4467 | 2080_00005‐1
D | 01‐VHHS936 | HP ECONOMIZER DRAIN | HHS9927 | HHS9929 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4468 | 2080_00005‐1
D | 01‐VHHS937 | HP ECONOMIZER DRAIN | HHS9930 | HHS9932 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4469 | 2080_00005‐1
D | 01‐VHHS938 | HP ECONOMIZER DRAIN | HHS9926 | HHS9312 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4470 | 2080_00005‐1
D | 01‐VHHS939 | HP ECONOMIZER VENT | HHS9951 | HHS9953 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4471 | 2080_00005‐1
D | 01‐VHHS940 | HP ECONOMIZER VENT | HHS9954 | HHS9956 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4472 | 2080_00005‐1
D | 01‐VHHS941 | HP ECONOMIZER VENT | HHS9957 | HHS9959 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4473 | 2080_00005‐1
D | 01‐VHHS942 | HP ECONOMIZER VENT | HHS9960 | HHS9962 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4474 | 2080_00005‐1
D | 01‐VHHS943 | HP ECONOMIZER VENT | HHS9963 | HHS9965 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4475 | 2080_00005‐1
D | 01‐VHHS944 | HP ECONOMIZER VENT | HHS9966 | HHS9968 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4476 | 2080_00005‐1
D | 01‐VHHS945 | HP ECONOMIZER VENT | HHS9969 | HHS9971 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4477 | 2080_00005‐1
D | 01‐VHHS946 | HP ECONOMIZER VENT | HHS9972 | HHS9974 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4478 | 2080_00005‐1
D | 01‐VHHS947 | HP ECONOMIZER VENT | HHS9975 | HHS9977 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4479 | 2080_00005‐1
D | 01‐VHHS961 | HP ECONOMIZER DRAIN | HHS9908 | HHS9909 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4480 | 2080_00005‐1
D | 01‐VHHS801 | HP SATURATED STEAM VENT | HHS8978 | HHS8978 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4481 | 2080_00005‐2
D | 01‐VHHS802 | HP SATURATED STEAM VENT | HHS8978 | HHS8978 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4482 | 2080_00005‐2
D | 01‐VHHS950 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS9807 | HHS9807 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4483 | 2080_00005‐2
D | 01‐VHHS951 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS9807 | HHS9807 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4484 | 2080_00005‐2
D | 01‐VHHS952 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS9808 | HHS9808 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4485 | 2080_00005‐2
D | 01‐VHHS953 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS9808 | HHS9808 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4486 | 2080_00005‐2
D | 01‐VHHS954 | HP DRUM PRESSURE INDICATOR ISOLATION | HHS8802 | HHS8802 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4487 | 2080_00005‐2
D | 01‐VHHS955 | HP DRUM PRESSURE INDICATOR ISOLATION | HHS8802 | HHS8802 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4488 | 2080_00005‐2
D | 01‐VHHS956 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS8801 | HHS8801 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4489 | 2080_00005‐2
D | 01‐VHHS957 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS8801 | HHS8801 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4490 | 2080_00005‐2
D | 01‐VHHS958 | HP DRUM NITROGEN SUPPLY NRV | HRG9103 | HHS8401 | Water/Steam | NA | NA | 2" | 2" | Stop Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23101 | 23.22 | 4491 | 2080_00005‐2
D | 01‐VHHS959 | HP DRUM NITROGEN SUPPLY ISOLATION | HHS8401 | HHS8401 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4492 | 2080_00005‐2
D | 01‐VHHS963 | HP DRUM LEVEL GAUGE ISOLATION | HHS9814 | HHS9814 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4493 | 2080_00005‐2
D | 01‐VHHS964 | HP DRUM LEVEL GAUGE ISOLATION | HHS9814 | HHS9815 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4494 | 2080_00005‐2
D | 01‐VHHS965 | HP DRUM LEVEL GAUGE DRAIN | HHS9934 | HHS9935 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4495 | 2080_00005‐2
D | 01‐VHHS966 | HP DRUM LEVEL GAUGE DRAIN | HHS9934 | HHS9934 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4496 | 2080_00005‐2
D | 01‐VHHS967 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9811 | HHS9811 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4497 | 2080_00005‐2
D | 01‐VHHS968 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9811 | HHS9811 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4498 | 2080_00005‐2
D | 01‐VHHS969 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9813 | HHS9813 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4499 | 2080_00005‐2
D | 01‐VHHS970 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9813 | HHS9813 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4500 | 2080_00005‐2
D | 01‐VHHS971 | HP DRUM LEVEL GAUGE ISOLATION | HHS9824 | HHS9824 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4501 | 2080_00005‐2
D | 01‐VHHS972 | HP DRUM LEVEL GAUGE DRAIN | HHS9937 | HHS9937 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4502 | 2080_00005‐2
D | 01‐VHHS973 | HP DRUM LEVEL GAUGE DRAIN | HHS9936 | HHS9938 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4503 | 2080_00005‐2
D | 01‐VHHS974 | HP DRUM LEVEL GAUGE DRAIN | HHS9936 | HHS9936 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4504 | 2080_00005‐2
D | 01‐VHHS975 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9821 | HHS9821 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4505 | 2080_00005‐2
D | 01‐VHHS976 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9821 | HHS9821 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4506 | 2080_00005‐2
D | 01‐VHHS977 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9823 | HHS9823 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4507 | 2080_00005‐2
D | 01‐VHHS978 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9823 | HHS9823 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4508 | 2080_00005‐2
D | 01‐VHHS979 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9818 | HHS9818 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4509 | 2080_00005‐2
D | 01‐VHHS980 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9818 | HHS9818 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4510 | 2080_00005‐2
D | 01‐VHHS981 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9820 | HHS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4511 | 2080_00005‐2
D | 01‐VHHS982 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9820 | HHS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4512 | 2080_00005‐2
D | 01‐VHHS983 | HP DRUM LEVEL GAUGE ISOLATION | HHS9824 | HHS9825 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4513 | 2080_00005‐2
D | 01‐VHHS984 | HP DRUM LEVEL GAUGE ISOLATION | HHS9826 | HHS9827 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4514 | 2080_00005‐2
D | 01‐VHHS985 | HP DRUM LEVEL GAUGE ISOLATION | HHS9826 | HHS9826 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4515 | 2080_00005‐2
D | 01‐VHHS986 | HP DRUM LEVEL GAUGE ISOLATION | HHS9816 | HHS9816 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4516 | 2080_00005‐2
D | 01‐VHHS987 | HP DRUM LEVEL GAUGE ISOLATION | HHS9816 | HHS9817 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4517 | 2080_00005‐2
D | 01‐VHHS988 | HP DRUM INLET CHEMICAL INJECTION ISOLATION | HHS9502 | HHS9502 | Water | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 4518 | 2080_00005‐2
D | 01‐VHHS989 | HP DRUM INLET CHEMICAL INJECTION CHECK VALVE | HHS9502 | HHS9502 | Water | NA | NA | 1" | 1" | Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23119 | 23.22 | 4519 | 2080_00005‐2
D | 01‐VHHS991 | HP DRUM WATER SAMPLE ISOLATION | HHS9603 | HHS9603 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4520 | 2080_00005‐2
D | 01‐VHHS992 | HP DRUM WATER SAMPLE ISOLATION | HHS9603 | HHS9603 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4521 | 2080_00005‐2
D | 01‐VHHS994 | HP SPARGING STEAM DRAIN | HHS9939 | HHS9939 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4522 | 2080_00005‐2
D | 01‐VHHS995 | HP SPARGING STEAM DRAIN | HHS9939 | HHS9940 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4523 | 2080_00005‐2
D | 01‐VHHS996 | HP SPARGING STEAM STRAINER DRAIN | HHS9941 | HHS9941 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4524 | 2080_00005‐2
D | 01‐VHHS997 | HP SPARGING STEAM STRAINER DRAIN | HHS9941 | HHS9942 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4525 | 2080_00005‐2
D | 01‐VHHS998 | HP SATURATED STEAM SAMPLE ISOLATION | HHS9605 | HHS9605 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23108 | 23.22 | 4526 | 2080_00005‐2
D | 01‐VHHS999 | HP SATURATED STEAM SAMPLE ISOLATION | HHS9605 | HHS9605 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23108 | 23.22 | 4527 | 2080_00005‐2
D | 01‐VHHS803 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8828 | HHS8828 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4528 | 2080_00005‐3
D | 01‐VHHS804 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8828 | HHS8828 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4529 | 2080_00005‐3
D | 01‐VHHS805 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8829 | HHS8829 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4530 | 2080_00005‐3
D | 01‐VHHS806 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8829 | HHS8829 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4531 | 2080_00005‐3
D | 01‐VHHS807 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8830 | HHS8830 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4532 | 2080_00005‐3
D | 01‐VHHS808 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8830 | HHS8830 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4533 | 2080_00005‐3
D | 01‐VHHS809 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8831 | HHS8831 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4534 | 2080_00005‐3
D | 01‐VHHS810 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8831 | HHS8831 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 4535 | 2080_00005‐3
D | 01‐VHHS811 | HP SUPERHEATER 1 TO 2 CROSSOVER VENT | HHS8984 | HHS8984 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 2741 | 884 | 189 | 473.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23105 | 23.22 | 4536 | 2080_00005‐3
D | 01‐VHHS812 | HP SUPERHEATER 1 TO 2 CROSSOVER VENT | HHS8984 | HHS8984 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 2741 | 884 | 189 | 473.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23105 | 23.22 | 4537 | 2080_00005‐3
D | 01‐VHHS813 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8832 | HHS8832 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4538 | 2080_00005‐3
D | 01‐VHHS814 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8832 | HHS8832 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4539 | 2080_00005‐3
D | 01‐VHHS815 | HP SUPERHEATER OUTLET PRESSURE INDICATOR ISOLATION | HHS8833 | HHS8833 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4540 | 2080_00005‐3
D | 01‐VHHS816 | HP SUPERHEATER OUTLET PRESSURE INDICATOR ISOLATION | HHS8833 | HHS8833 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4541 | 2080_00005‐3
D | 01‐VHHS818 | HP SUPERHEATER OUTLET DRAIN | HHS8313 | HHS8313 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23104 | 23.22 | 4542 | 2080_00005‐3
D | 01‐VHHS819 | HP SUPERHEATER OUTLET DRAIN | HHS8313 | HHS8314 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23104 | 23.22 | 4543 | 2080_00005‐3
D | 01‐VHHS820 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8835 | HHS8835 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4544 | 2080_00005‐3
D | 01‐VHHS821 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8835 | HHS8835 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4545 | 2080_00005‐3
D | 01‐VHHS822 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8837 | HHS8837 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4546 | 2080_00005‐3
D | 01‐VHHS823 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8837 | HHS8837 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4547 | 2080_00005‐3
D | 01‐VHHS824 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8839 | HHS8839 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4548 | 2080_00005‐3
D | 01‐VHHS825 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8839 | HHS8839 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4549 | 2080_00005‐3
D | 01‐VHHS826 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8841 | HHS8841 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4550 | 2080_00005‐3
D | 01‐VHHS827 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8841 | HHS8841 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4551 | 2080_00005‐3
D | 01‐VHHS828 | HP SUPERHEATED STEAM SAMPLE ISOLATION | HHS8607 | HHS8607 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 2534 | 1098 | 174.7 | 592 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23108 | 23.22 | 4552 | 2080_00005‐3
D | 01‐VHHS829 | HP SUPERHEATED STEAM SAMPLE ISOLATION | HHS8607 | HHS8607 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 2534 | 1098 | 174.7 | 592 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23108 | 23.22 | 4553 | 2080_00005‐3
D | 01‐VHHS830 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8842 | HHS8842 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4554 | 2080_00005‐3
D | 01‐VHHS831 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8842 | HHS8842 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4555 | 2080_00005‐3
D | 01‐VHHS832 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8843 | HHS8843 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4556 | 2080_00005‐3
D | 01‐VHHS833 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8843 | HHS8843 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4557 | 2080_00005‐3
D | 01‐VHHS834 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8844 | HHS8844 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4558 | 2080_00005‐3
D | 01‐VHHS835 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8844 | HHS8844 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4559 | 2080_00005‐3
D | 01‐VHHS836 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8845 | HHS8845 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4560 | 2080_00005‐3
D | 01‐VHHS837 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8845 | HHS8845 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4561 | 2080_00005‐3
D | 01‐VHHS838 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HHS8846 | HHS8846 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4562 | 2080_00005‐3
D | 01‐VHHS839 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HHS8846 | HHS8846 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4563 | 2080_00005‐3
D | 01‐VHHS840 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HHS8847 | HHS8847 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4564 | 2080_00005‐3
D | 01‐VHHS841 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HHS8847 | HHS8847 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4565 | 2080_00005‐3
D | 01‐VHHS842 | HP INTERSTAGE ATTEMPERATOR COOLING WATER STRAINER DRAIN | HHS8318 | HHS8318 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 4566 | 2080_00005‐3
D | 01‐VHHS843 | HP INTERSTAGE ATTEMPERATOR COOLING WATER STRAINER DRAIN | HHS8318 | HHS8316 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 4567 | 2080_00005‐3
D | 01‐VHHS846 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8848 | HHS8848 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4568 | 2080_00005‐3
D | 01‐VHHS847 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8848 | HHS8848 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4569 | 2080_00005‐3
D | 01‐VHHS848 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8849 | HHS8849 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4570 | 2080_00005‐3
D | 01‐VHHS849 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8849 | HHS8849 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4571 | 2080_00005‐3
D | 01‐VHHS850 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8850 | HHS8850 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4572 | 2080_00005‐3
D | 01‐VHHS851 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8850 | HHS8850 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4573 | 2080_00005‐3
D | 01‐VHHS852 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8851 | HHS8851 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4574 | 2080_00005‐3
D | 01‐VHHS853 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8851 | HHS8851 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 4575 | 2080_00005‐3
D | 01‐VHHS863 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DRAIN | HHS8319 | HHS8319 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 4576 | 2080_00005‐3
D | 01‐VHHS864 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DRAIN | HHS8319 | HHS8322 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 4577 | 2080_00005‐3
D | 01‐VHHS865 | HP INTERSTAGE ATTEMPERATOR COOLING WATER VENT | HHS8321 | HHS8321 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 1032 | 189 | 555.6 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS971 on valve drawing 2080_23113 Rev D | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 4578 | 2080_00005‐3
D | 01‐VHHS866 | HP INTERSTAGE ATTEMPERATOR COOLING WATER VENT | HHS8321 | HHS8320 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 1032 | 189 | 555.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 4579 | 2080_00005‐3
D | 01‐VHHS867 | HP SUPERHEATER 1 INLET DRAIN POT CLEANOUT DRAIN | HHS8323 | HHS8323 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23114 | 23.22 | 4580 | 2080_00005‐3
D | 01‐VHHS868 | HP SUPERHEATER 1 INLET DRAIN POT CLEANOUT DRAIN | HHS8323 | HHS8323 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23114 | 23.22 | 4581 | 2080_00005‐3
D | 01‐VHHS871 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8853 | HHS8853 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW | SPARE_423 on valve drawing 2080_23110 Rev D | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4582 | 2080_00005‐3
D | 01‐VHHS872 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8852 | HHS8852 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4583 | 2080_00005‐3
D | 01‐VHHS873 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8853 | HHS8853 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4584 | 2080_00005‐3
D | 01‐VHHS874 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8852 | HHS8852 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW | SPARE_424 on valve drawing 2080_23110 Rev D | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 4585 | 2080_00005‐3
D | 01‐VHHS909 | HP INTERSTAGE ATTEMPERATOR DRAIN POT CLEANOUT DRAIN | HHS9315 | HHS9315 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2741 | 1032 | 189 | 555.6 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23115 | 23.22 | 4586 | 2080_00005‐3
D | 01‐VHHS910 | HP INTERSTAGE ATTEMPERATOR DRAIN POT CLEANOUT DRAIN | HHS9315 | HHS9315 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2741 | 1032 | 189 | 555.6 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23115 | 23.22 | 4587 | 2080_00005‐3
D | 01‐VHLS801 | PREHEATER DRAIN | HLS8901 | HLS8901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4588 | 2080_00006‐1
D | 01‐VHLS802 | PREHEATER DRAIN | HLS8901 | HLS8902 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 9 & 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4589 | 2080_00006‐1
D | 01‐VHLS803 | LP FEEDWATER INLET PRESSURE TRANSMITTER ISOLATION | HLS8801 | HLS8801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4590 | 2080_00006‐1
D | 01‐VHLS804 | LP FEEDWATER INLET PRESSURE TRANSMITTER ISOLATION | HLS8801 | HLS8801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4591 | 2080_00006‐1
D | 01‐VHLS807 | PREHEATER DRAIN | HLS8905 | HLS8905 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4592 | 2080_00006‐1
D | 01‐VHLS810 | PREHEATER DRAIN | HLS8905 | HLS8906 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4593 | 2080_00006‐1
D | 01‐VHLS823 | PREHEATER DRAIN | HLS9907 | HLS8904 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 9 & 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4594 | 2080_00006‐1
D | 01‐VHLS824 | PREHEATER DRAIN | HLS9947 | HLS8903 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 9 & 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4595 | 2080_00006‐1
D | 01‐VHLS829 | PREHEATER DRAIN | HLS8907 | HLS8907 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW | SPARE_27 on valve drawing 2080_23125 Rev D | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4596 | 2080_00006‐1
D | 01‐VHLS830 | PREHEATER DRAIN | HLS8907 | HLS8908 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW | SPARE_28 on valve drawing 2080_23125 Rev D | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4597 | 2080_00006‐1
D | 01‐VHLS851 | PREHEATER INLET VENT | HLS8951 | HLS8951 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW | SPARE_134 on valve drawing 2080_23120 Rev D | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4598 | 2080_00006‐1
D | 01‐VHLS852 | PREHEATER INLET VENT | HLS8951 | HLS8952 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 356 | 41.4 | 180 | 800 | 800 | SW | SW | SPARE_398 on valve drawing 2080_23120 Rev D | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4599 | 2080_00006‐1
D | 01‐VHLS902 | PREHEATER DRAIN | HLS9901 | HLS9901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4600 | 2080_00006‐1
D | 01‐VHLS903 | PREHEATER DRAIN | HLS9901 | HLS9902 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4601 | 2080_00006‐1
D | 01‐VHLS906 | PREHEATER VENT | HLS9955 | HLS9956 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW | Tag previously 01‐VHLS909 (redundant with LB valve) | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4602 | 2080_00006‐1
D | 01‐VHLS910 | PREHEATER VENT | HLS9958 | HLS9959 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4603 | 2080_00006‐1
D | 01‐VHLS911 | PREHEATER DRAIN | HLS9903 | HLS9905 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4604 | 2080_00006‐1
D | 01‐VHLS912 | PREHEATER DRAIN | HLS9906 | HLS9907 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4605 | 2080_00006‐1
D | 01‐VHLS913 | PREHEATER DRAIN | HLS9942 | HLS9944 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4606 | 2080_00006‐1
D | 01‐VHLS914 | PREHEATER VENT | HLS9961 | HLS9962 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4607 | 2080_00006‐1
D | 01‐VHLS915 | PREHEATER VENT | HLS9964 | HLS9965 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4608 | 2080_00006‐1
D | 01‐VHLS916 | PREHEATER DRAIN | HLS9945 | HLS9947 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4609 | 2080_00006‐1
D | 01‐VHLS917 | PREHEATER VENT | HLS9967 | HLS9968 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4610 | 2080_00006‐1
D | 01‐VHLS918 | PREHEATER DRAIN | HLS9948 | HLS9949 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4611 | 2080_00006‐1
D | 01‐VHLS919 | PREHEATER VENT | HLS9970 | HLS9971 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4612 | 2080_00006‐1
D | 01‐VHLS920 | PREHEATER DRAIN | HLS9910 | HLS9912 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4613 | 2080_00006‐1
D | 01‐VHLS921 | PREHEATER DRAIN | HLS9912 | HLS9913 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 9 & 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4614 | 2080_00006‐1
D | 01‐VHLS922 | PREHEATER VENT | HLS9972 | HLS9973 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4615 | 2080_00006‐1
D | 01‐VHLS984 | PREHEATER VENT | HLS9952 | HLS9953 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4616 | 2080_00006‐1
D | 01‐VHBD801 | BLOWDOWN TANK PRESSURE INDICATOR ISOLATION | HBD9801 | HBD9801 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23123 | 23.22 | 4617 | 2080_00007‐1
D | 01‐VHBD802 | BLOWDOWN TANK PRESSURE TRANSMITTER ISOLATION | HBD9802 | HBD9802 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23123 | 23.22 | 4618 | 2080_00007‐1
D | 01‐VHBD803 | BLOWDOWN TANK LEVEL GAUGE ISOLATION | HBD9803 | HBD9803 | Water/Steam | NA | NA | 3/4" | 3/4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23127 | 23.22 | 4619 | 2080_00007‐1
D | 01‐VHBD804 | BLOWDOWN TANK LEVEL GAUGE ISOLATION | HBD9804 | HBD9804 | Water/Steam | NA | NA | 3/4" | 3/4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23127 | 23.22 | 4620 | 2080_00007‐1
D | 01‐VHBD805 | BLOWDOWN TANK LEVEL TRANSMITTER ISOLATION | HBD9805 | HBD9805 | Water/Steam | NA | NA | 3/4" | 3/4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23127 | 23.22 | 4621 | 2080_00007‐1
D | 01‐VHBD806 | BLOWDOWN TANK LEVEL TRANSMITTER ISOLATION | HBD9806 | HBD9806 | Water/Steam | NA | NA | 3/4" | 3/4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23127 | 23.22 | 4622 | 2080_00007‐1
D | 01‐VHBD901 | BLOWDOWN TANK LOW POINT DRAIN | HBD9901 | HBD9901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23125 | 23.22 | 4623 | 2080_00007‐1
D | 01‐VHBD902 | BLOWDOWN TANK LEVEL GAUGE DRAIN | HBD9920 | HBD9920 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW | 01‐VHLS996 on valve drawing 2080_23106 Rev D | 78 | 5 | 9 | ‐ | HP Valve | 2080_23106 | 23.22 | 4624 | 2080_00007‐1
D | 01‐VHBD903 | BLOWDOWN TANK LEVEL GAUGE DRAIN | HBD9920 | HBD9920 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS983 on valve drawing 2080_23106 Rev D | 78 | 5 | 9 | ‐ | HP Valve | 2080_23106 | 23.22 | 4625 | 2080_00007‐1
D | 01‐VHBD907 | BLOWDOWN QUENCH WATER DRAIN | HBD9914 | HBD9914 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23113 | 23.22 | 4626 | 2080_00007‐1
D | 01‐VHBD908 | BLOWDOWN QUENCH WATER DRAIN | HBD9914 | HBD9914 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23113 | 23.22 | 4627 | 2080_00007‐1
D | 01‐VHBD909 | BLOWDOWN QUENCH WATER BYPASS | HBD9111 | HBD9112 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS984 on valve drawing 2080_23106 Rev D | 78 | 5 | 9 | ‐ | HP Valve | 2080_23106 | 23.22 | 4628 | 2080_00007‐1
E | 01‐VHHS861 | HP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HHS8931 | HHS8931 | Water | NA | NA | 2" | 2" | Y globe valve | SA‐106 C | SA‐106 C | SA‐105 | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | SW | SW | TBD on valve drawing 2080_23103 Rev C | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4629 | 2080_00007‐1
E | 01‐VHHS862 | HP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HHS8931 | HHS8931 | Water | NA | NA | 2" | 2" | Y globe valve | SA‐106 C | SA‐106 C | SA‐105 | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | SW | SW | TBD on valve drawing 2080_23103 Rev C | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4630 | 2080_00007‐1
D | 01‐VHHS960 | HP EVAPORATOR DRAIN | HHS9994 | HBD9906 | Water | NA | NA | 2" | 2" | Y globe valve | SA‐106 C | SA‐106 C | SA‐105N | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 4631 | 2080_00007‐1
D | 01‐VHIS908 | IP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HIS9934 | HIS9934 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105 | 812 | 522 | 56 | 272.2 | 800 | 800 | SW | SW | SPARE 01‐VHLS949 on valve drawing 2080_23125 Rev D | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4632 | 2080_00007‐1
D | 01‐VHIS909 | IP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HIS9934 | HIS9934 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105 | 812 | 522 | 56 | 272.2 | 800 | 800 | SW | SW | SPARE 01‐VHLS939 on valve drawing 2080_23125 Rev D | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4633 | 2080_00007‐1
D | 01‐VHLS928 | LP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HLS9932 | HLS9932 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105 | 196 | 386 | 13.5 | 196.5 | 800 | 800 | SW | SW | SPARE 01‐VHLS964 on valve drawing 2080_23125 Rev D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4634 | 2080_00007‐1
D | 01‐VHLS929 | LP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HLS9932 | HLS9932 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105 | 196 | 386 | 13.5 | 196.5 | 800 | 800 | SW | SW | SPARE 01‐VHLS965 on valve drawing 2080_23125 Rev D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4635 | 2080_00007‐1
D | 01‐MOV‐HLS904 | LP STEAM SPARGING | HLS9125 | HLS9152 | Steam | MOVDIG | FIP | 3" | 3" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 425 | 454 | 29.3 | 234.4 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 638 | 44 | 8 | ‐ | HP Valve | 2080_23326 | 23.3 | 4636 | 2080_00003‐1
D | 01‐MOV‐HLS905 | LP STEAM STARTUP VENT STOP | HLS9988 | HLS9993 | Steam | MOVDIG | FIP | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 247 | 623 | 17 | 328.5 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 196 | 14 | 2 | ‐ | HP Valve | 2080_23329 | 23.3 | 4637 | 2080_00003‐2
D | 01‐MOV‐HLS906 | LP STEAM OUTLET STOP | HLS9165 | HLS9166 | Steam | MOVDIG | FIP | 14" | 14" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 131 | 623 | 9 | 328.5 | 150 | 150 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 196 | 14 | 2 | ‐ | HP Valve | 2080_23303 | 23.3 | 4638 | 2080_00003‐2
D | 01‐MOV‐HIS901 | IP FEEDWATER INLET STOP VALVE | HIS9101 | HIS9102 | Water | MOVDIG | FIP | 6" | 6" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 2100 | 145 | 3 | Bypass Equalizer Type 4 | HP Valve | 2080_23328 | 23.3 | 4639 | 2080_00004‐1
D | 01‐MOV‐HIS903 | IP ECONOMIZER VENT STOP | HIS9978 | HIS9956 | Water | MOVDIG | FIP | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 2100 | 145 | 4 & 3 | ‐ | HP Valve | 2080_23306 | 23.3 | 4640 | 2080_00004‐1
D | 01‐MOV‐HIS904 | IP FEEDWATER FGH STOP VALVE | HIS9914 | HIS9196 | Water | MOVDIG | FIP | 4" | 4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 2100 | 145 | 3 & 4 | Bypass Equalizer Type 4 | HP Valve | 2080_23319 | 23.3 | 4641 | 2080_00004‐1
D | 01‐MOV‐HIS909 | IP SPARGING STEAM STOP | HIS9140 | HIS9140 | Steam | MOVDIG | FIP | 3" | 3" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 656 | 498 | 45.2 | 259 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 638 | 44 | 8 | ‐ | HP Valve | 2080_23305 | 23.3 | 4642 | 2080_00004‐2
D | 01‐MOV‐HIS910 | IP TO DA PEGGING | HIS9202 | HIS9202 | Steam | MOVDIG | FIP | 3" | 3" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 502 | 43 | 261.1 | 1500 | 1500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | HP Valve | 2080_23325 | 23.3 | 4643 | 2080_00004‐2
D | 01‐MOV‐HIS906 | IP SUPERHEATER OUTLET VENT | HIS9966 | HIS9967 | Steam | MOVDIG | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | HP Valve | 2080_23310 | 23.3 | 4644 | 2080_00004‐3
D | 01‐MOV‐HIS908 | IP STEAM STOP | HIS9147 | HIS9190 | Steam | MOVDIG | FIP | 8" | 8" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 624 | 622 | 43 | 327.6 | 300 SPL | 300 SPL | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | Bypass Equalizer Type 4 | HP Valve | 2080_23304 | 23.3 | 4645 | 2080_00004‐3
D | 01‐MOV‐HRS904 | REHEAT OUTLET STARTUP VENT STOP | HRS9973 | HRS9976 | Steam | MOVDIG | FIP | 4" | 4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 | 2500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 5 | ‐ | HP Valve | 2080_23332 | 23.3 | 4646 | 2080_00004‐4
D | 01‐MOV‐HRS912 | RHT ATTEMPERATOR SPRAY WATER STOP | HRS9178 | HRS9179 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23316 | 23.3 | 4647 | 2080_00004‐4
D | 01‐MOV‐HHS901 | HP FEEDWATER STOP | HHS9105 | HHS9199 | Water | MOVDIG | FIP | 12" | 12" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2000 | 2000 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 6150 | 424 | 7 & 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23321 | 23.3 | 4648 | 2080_00005‐1
D | 01‐MOV‐HHS902 | HP ECONOMIZER VENT | HHS9977 | HHS9978 | Water | MOVDIG | FIP | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23307 | 23.3 | 4649 | 2080_00005‐1
D | 01‐MOV‐HHS904 | HP SPARGING STEAM | HHS9161 | HHS9218 | Steam | MOVDIG | FIP | 4" | 4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 1500 SPL | 1500 SPL | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 & 8 | Bypass Equalizer Type 4 | HP Valve | 2080_23331 | 23.3 | 4650 | 2080_00005‐2
D | 01‐MOV‐HHS906 | HP STEAM OUTLET STOP | HHS9220 | HHS9189 | Steam | MOVDIG | FIP | 16" | 16" | Parallel Slide Gate | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2150 SPL | 2150 SPL | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | Bypass Equalizer Type 4 | HP Valve | 2080_23322 | 23.3 | 4651 | 2080_00005‐3
D | 01‐MOV‐HHS907 | HP STEAM OUTLET STOP VALVE BYPASS | HHS9192 | HHS9192 | Steam | MOVDIG | FIP | 12" | 12" | Gate Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 SPL | 2500 SPL | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | Bypass Equalizer Type 4 | HP Valve | 2080_23324 | 23.3 | 4652 | 2080_00005‐3
D | 01‐MOV‐HHS908 | HP ATTEMPERATOR SPRAY WATER STOP | HHS9195 | HHS9196 | Water | MOVDIG | FIP | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23317 | 23.3 | 4653 | 2080_00005‐3
D | 01‐MOV‐HHS913 | HP SUPERHEATER OUTLET VENT | HHS9987 | HHS9988 | Steam | MOVDIG | FIP | 2" | 2" | Y globe valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23311 | 23.3 | 4654 | 2080_00005‐3
D | 01‐MOV‐HLS901 | LP FEEDWATER INLET STOP | HLS9102 | HLS9103 | Water | MOVDIG | FIP | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 | 300 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23302 | 23.3 | 4655 | 2080_00006‐1
D | 01‐MOV‐HLS907 | LP ECONOMIZER VENT | HLS9973 | HLS9974 | Water | MOVDIG | FIP | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 901 | 62 | 2 & 1 | ‐ | HP Valve | 2080_23306 | 23.3 | 4656 | 2080_00006‐1
D | 01‐YCV‐HHS902 | HP SH #1 DRAIN POT | HHS9305 | HBD9903 | Water | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 2741 | 1032 | 189 | 555.6 | 2500 | 2500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN/ CLOSED LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23314 | 23.3 | 4657 | 2080_00007‐1
D | 01‐YCV‐HHS903 | HP ATTEMPERATOR LOOP DRAIN POT | HHS9307 | HBD9902 | Water | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2741 | 1032 | 189 | 555.6 | 2500 LTD | 2500 LTD | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN / CLOSE LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23313 | 23.3 | 4658 | 2080_00007‐1
D | 01‐YCV‐HIS905 | IP STEAM OUTLET DRAIN POT | HIS9927 | HBD9909 | Steam | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 1500 | 1500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 935 | 65 | 9 & 4 | ‐ | HP Valve | 2080_23312 | 23.3 | 4659 | 2080_00007‐1
D | 01‐YCV‐HIS906 | IP STEAM OUTLET DRAIN POT | HIS9933 | HBD9913 | Steam | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 1500 | 1500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 935 | 65 | 9 & 4 | ‐ | HP Valve | 2080_23327 | 23.3 | 4660 | 2080_00007‐1
D | 01‐YCV‐HLS909 | LP SUPERHEATER OUTLET DRAIN POT DRAIN | HLS9936 | HBD9912 | Water | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 624 | 9 | 328.7 | 1500 | 1500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN / CLOSE LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 196 | 14 | 9 & 2 | ‐ | HP Valve | 2080_23312 | 23.3 | 4661 | 2080_00007‐1
D | 01‐YCV‐HLS910 | LP SUPERHEATER OUTLET DRAIN | HLS9933 | HBD9923 | Water | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 624 | 9 | 328.7 | 1500 | 1500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN / CLOSE LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 196 | 14 | 9 & 2 | ‐ | HP Valve | 2080_23312 | 23.3 | 4662 | 2080_00007‐1
D | 01‐YCV‐HRS905 | REHEAT ATTEMPERATOR LOOP DRAIN POT | HRS9945 | HBD9908 | Water | POVPOS | FIP | 2 1/2" | 2 1/2" | Y globe valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 624 | 946 | 43 | 508 | 1500 | 1500 | BW | BW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN / CLOSE LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 935 | 65 | 9 & 5 | ‐ | HP Valve | 2080_23330 | 23.3 | 4663 | 2080_00007‐1
D | 01‐YTS‐HLS995 | LP SPARGING STEAM STRAINER | HLS9178 | HLS9178 | Steam | NA | NA | 3" | 3" | Y‐Type Strainer | SA‐106 B | SA‐106 B | SA‐105 | 162 | 372 | 11.2 | 188.7 | 2500 | 2500 | BW | BW | Mesh Size 40 and 1" SW blowdown connection | 196 | 14 | 2 | ‐ | HP Valve | 2080_23702 | 23.33 | 4664 | 2080_00003‐1
D | 01‐YTS‐HIS995 | IP SPARGING STEAM STRAINER | HIS9107 | HIS9107 | Steam | NA | NA | 3" | 3" | Y‐Type Strainer | SA‐106 B | SA‐106 B | SA‐105 | 656 | 498 | 45.2 | 259 | 2500 | 2500 | BW | BW | Mesh Size 40 and 1" SW blowdown connection | 935 | 65 | 4 | ‐ | HP Valve | 2080_23701 | 23.33 | 4665 | 2080_00004‐2
D | 01‐YTS‐HRS901 | RHT ATTEMPERATOR SPRAY WATER STRAINER | HRS9176 | HRS9176 | Water | NA | NA | 2 1/2" | 2 1/2" | Y‐Type Strainer | SA‐106 B | SA‐106 B | SA‐105 | 624 | 1096 | 43 | 591.1 | 2500 | 2500 | BW | BW | Mesh Size 100 and 1" SW blowdown connection | 935 | 65 | 5 | ‐ | HP Valve | 2080_23652 | 23.33 | 4666 | 2080_00004‐4
D | 01‐YTS‐HHS995 | HP SPARGING STEAM STRAINER | HHS9221 | HHS9221 | Steam | NA | NA | 4" | 4" | Y‐Type Strainer | SA‐106 B | SA‐106 B | SA‐105 | 2773 | 684 | 191.2 | 362.4 | 1500 SPL | 1500 SPL | BW | BW | Mesh Size 40 and 1" SW blowdown connection | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23653 | 23.33 | 4667 | 2080_00005‐2
D | 01‐YTS‐HHS901 | HP ATTEMPERATOR SPRAY WATER STRAINER | HHS9196 | HHS9196 | Water | NA | NA | 2 1/2" | 2 1/2" | Y‐Type Strainer | SA‐106 C | SA‐106 C | SA‐105 | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | Mesh Size 100 and 1" SW blowdown connection | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23651 | 23.33 | 4668 | 2080_00005‐3
D | 01‐MOV‐HLS902 | LP SUPERHEATER OUTLET VENT | HLS9987 | HLS9988 | Steam | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 131 | 623 | 9 | 328.5 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 196 | 14 | 2 | ‐ | ValvTechnologies | 2080_23619 | 23.36 | 4669 | 2080_00003‐2
D | 01‐MOV‐HIS902 | IP SUPERHEATER OUTLET VENT | HIS9966 | HIS9966 | Steam | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 624 | 622 | 43 | 327.6 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23616 | 23.36 | 4670 | 2080_00004‐3
D | 01‐MOV‐HRS911 | REHEAT VENT | HRS9973 | HRS9973 | Steam | MOVDIG | FIP | 4" | 4" | Ball valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 5 | ‐ | ValvTechnologies | 2080_23621 | 23.36 | 4671 | 2080_00004‐4
D | 01‐MOV‐HHS903 | HP CASCADING BLOW DOWN ISOLATION | HHS9943 | HHS9943 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23611 | 23.36 | 4672 | 2080_00005‐2
D | 01‐MOV‐HHS905 | HP SUPERHEATER OUTLET VENT | HHS9986 | HHS9987 | Steam | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23610 | 23.36 | 4673 | 2080_00005‐3
D | 01‐MOV‐HBD901 | HP BD MANIFOLD DRAIN | HBD9915 | HBD9916 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 58 | 750 | 4 | 399 | 150 | 150 | SW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 78 | 5 | 9 | ‐ | ValvTechnologies | 2080_23603 | 23.36 | 4674 | 2080_00007‐1
D | 01‐MOV‐HBD902 | IP BD MANIFOLD DRAIN | HBD9917 | HBD9918 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 58 | 750 | 4 | 399 | 150 | 150 | SW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 78 | 5 | 9 | ‐ | ValvTechnologies | 2080_23604 | 23.36 | 4675 | 2080_00007‐1
D | 01‐MOV‐HBD903 | LP BD MANIFOLD DRAIN | HBD9919 | HBD9921 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 58 | 750 | 4 | 399 | 150 | 150 | SW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 78 | 5 | 9 | ‐ | ValvTechnologies | 2080_23605 | 23.36 | 4676 | 2080_00007‐1
D | 01‐MOV‐HHS909 | HP INTERMITTENT BLOWDOWN STOP | HHS9947 | HHS9947 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23606 | 23.36 | 4677 | 2080_00007‐1
D | 01‐MOV‐HHS910 | HP SH #1 DRAIN POT STOP | HHS9305 | HHS9305 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23608 | 23.36 | 4678 | 2080_00007‐1
D | 01‐MOV‐HHS911 | HP ATTEMPERATOR DRAIN POT STOP | HHS9307 | HHS9307 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2741 | 1032 | 189 | 555.6 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23609 | 23.36 | 4679 | 2080_00007‐1
D | 01‐MOV‐HHS912 | HP INTERMITTENT BLOWDOWN STOP | HHS9945 | HHS9945 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23607 | 23.36 | 4680 | 2080_00007‐1
D | 01‐MOV‐HIS905 | IP CONTINUOUS BLOWDOWN STOP | HIS9912 | HIS9912 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 656 | 498 | 45.2 | 259 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23617 | 23.36 | 4681 | 2080_00007‐1
D | 01‐MOV‐HIS915 | IP DRAIN POT STOP | HIS9927 | HIS9927 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 624 | 622 | 43 | 327.6 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23614 | 23.36 | 4682 | 2080_00007‐1
D | 01‐MOV‐HIS916 | IP INTERMITTENT BLOWDOWN STOP | HIS9914 | HIS9914 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 812 | 522 | 56 | 272.2 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23612 | 23.36 | 4683 | 2080_00007‐1
D | 01‐MOV‐HIS917 | IP INTERMITTENT BLOWDOWN STOP | HIS9916 | HIS9916 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 812 | 522 | 56 | 272.2 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23613 | 23.36 | 4684 | 2080_00007‐1
D | 01‐MOV‐HIS918 | IP OUTLET DRAIN POT STOP | HIS9933 | HIS9933 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 624 | 622 | 43 | 327.6 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23615 | 23.36 | 4685 | 2080_00007‐1
D | 01‐MOV‐HLS908 | LP INTERMITTENT BLOWDOWN STOP | HLS9934 | HLS9934 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 196 | 386 | 13.5 | 196.5 | 150 | 150 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 196 | 14 | 2 | ‐ | ValvTechnologies | 2080_23618 | 23.36 | 4686 | 2080_00007‐1
D | 01‐MOV‐HRS914 | REHEAT ATTEMPERATOR LOOP DRAIN POT | HRS9945 | HRS9945 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 946 | 43 | 508 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 5 | ‐ | ValvTechnologies | 2080_23620 | 23.36 | 4687 | 2080_00007‐1
D | 01‐VHLS995 | LP DRAIN POT STOP | HLS9936 | HLS9936 | Water | NA | NA | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 131 | 624 | 9 | 328.7 | 300 | 300 | SW | SW |  | 196 | 14 | 2 | ‐ | ValvTechnologies | 2080_23601 | 23.36 | 4688 | 2080_00007‐1
D | 01‐VHLS996 | LP DRAIN POT STOP | HLS9933 | HLS9933 | Water | NA | NA | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 131 | 624 | 9 | 328.7 | 300 | 300 | SW | SW |  | 196 | 14 | 2 | ‐ | ValvTechnologies | 2080_23602 | 23.36 | 4689 | 2080_00007‐1
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 4690 | 2080_00003‐1
D | 01‐PRV‐HLS998 | LP DRUM PRESSURE RELIEF VALVE 2 | LP DRUM | HLS9704 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23211 | 23.03 | 4691 | 2080_00003‐1
D | 01‐PRV‐HLS999 | LP STEAM OUTLET PRESSURE RELIEF VALVE | HLS9165 | HLS9706 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 623 | 9 | 328.5 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23213 | 23.03 | 4692 | 2080_00003‐2
D | 01‐PRV‐HIS995 | IP ECONOMIZER INLET PRESSURE RELIEF VALVE | HIS9103 | HIS9701 | Water | NA | NA | 2" | 3" | PRV | SA‐106 B | SA‐106 B | SA‐351 Gr CF8M | 1400 | 550 | 96.5 | 288 | 1500 | 300 | FL | FL |  | 2100 | 145 | 9 & 3 | ‐ | Trillium | 2080_23228 | 23.03 | 4693 | 2080_00004‐1
D | 01‐PRV‐HIS997 | IP DRUM PRESSURE RELIEF VALVE 1 | IP DRUM | HIS9702 | Steam | NA | NA | 3" | 4" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 493 | 43 | 256.1 | 300 | 150 | FL | FL |  | 935 | 65 | 4 | ‐ | Trillium | 2080_23222 | 23.03 | 4694 | 2080_00004‐2
D | 01‐PRV‐HIS998 | IP DRUM PRESSURE RELIEF VALVE 2 | IP DRUM | HIS9703 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 493 | 43 | 256.1 | 300 | 150 | FL | FL |  | 935 | 65 | 4 | ‐ | Trillium | 2080_23221 | 23.03 | 4695 | 2080_00004‐2
D | 01‐PRV‐HIS999 | IP STEAM OUTLET PRESSURE RELIEF VALVE | HIS9146 | HIS9704 | Steam | NA | NA | 3" | 4" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 622 | 43 | 327.6 | 300 | 150 | FL | FL |  | 935 | 65 | 4 | ‐ | Trillium | 2080_23223 | 23.03 | 4696 | 2080_00004‐3
D | 01‐PRV‐HRS997 | COLD REHEAT PRESSURE RELIEF VALVE 1 | HRS9192 | HRS9705 | Steam | NA | NA | 6" | 10" | PRV | SA‐335 P11 | SA‐335 P11 | SA‐216 Gr WCC | 624 | 752 | 43 | 400.2 | 600 | 150 | FL | FL |  | 935 | 65 | 5 | ‐ | Trillium | 2080_23225 | 23.03 | 4697 | 2080_00004‐4
D | 01‐PRV‐HRS998 | COLD REHEAT PRESSURE RELIEF VALVE 2 | HRS9192 | HRS9706 | Steam | NA | NA | 8" | 2 x 10" | PRV | SA‐335 P11 | SA‐335 P11 | SA‐216 Gr WCC | 624 | 752 | 43 | 400.2 | 600 | 150 | FL | FL |  | 935 | 65 | 5 | ‐ | Trillium | 2080_23224 | 23.03 | 4698 | 2080_00004‐4
D | 01‐PRV‐HRS999 | HOT REHEAT PRESSURE RELIEF VALVE | HRS9195 | HRS9707 | Steam | NA | NA | 6" | 8" | PRV | SA‐335 P91 | SA‐335 P91 | SA‐351 Gr CF8M | 624 | 1096 | 43 | 591.1 | 600 | 300 | FL | FL |  | 935 | 65 | 5 | ‐ | Trillium | 2080_23226 | 23.03 | 4699 | 2080_00004‐4
D | 01‐PRV‐HHS997 | HP DRUM PRESSURE RELIEF VALVE 1 | HP DRUM | HHS9701 | Steam | NA | NA | 2.5" | 6" | PRV | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2741 | 683 | 189 | 361.5 | 2500 | 300 | FL | FL |  | 4112 | 284 | 7 | ‐ | Trillium | 2080_23232 | 23.03 | 4700 | 2080_00005‐2
D | 01‐PRV‐HHS998 | HP DRUM PRESSURE RELIEF VALVE 2 | HP DRUM | HHS9702 | Steam | NA | NA | 3" | 6" | PRV | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2741 | 683 | 189 | 361.5 | 2500 | 300 | FL | FL |  | 4112 | 284 | 7 | ‐ | Trillium | 2080_23231 | 23.03 | 4701 | 2080_00005‐2
D | 01‐PRV‐HHS999 | HP STEAM OUTLET PRESSURE RELIEF VALVE | HHS9220 | HHS9703 | Steam | NA | NA | 3" | 6" | PRV | SA‐335 P91 | SA‐335 P91 | SA‐217 Gr C12A | 2534 | 1098 | 174.7 | 592 | 2500 | 300 | FL | FL |  | 4112 | 284 | 7 | ‐ | Trillium | 2080_23233 | 23.03 | 4702 | 2080_00005‐3
E | 01‐PRV‐HLS901 | PREHEATER EXT HEAT EXCHANGER PRESSURE RELIEF VALVE | HLS9174 | HLS9701 | Water | NA | NA | 1" | 2" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 455 | 41.4 | 235 | 300 | 300 | FL | FL |  | 901 | 62 | 9 & 1 | ‐ | Trillium | 2080_23201 | 23.03 | 4703 | 2080_00006‐1
E | 01‐PRV‐HLS902 | PREHEATER EXT HEAT EXCHANGER PRESSURE RELIEF VALVE | HLS9113 | HLS9702 | Water | NA | NA | 1" | 2" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 490 | 41.4 | 254.7 | 300 | 300 | FL | FL |  | 901 | 62 | 9 & 1 | ‐ | Trillium | 2080_23202 | 23.03 | 4704 | 2080_00006‐1
D | 01‐PRV‐HLS994 | PREHEATER INLET PILOT OPERATED RELIEF VALVE | HLS9104 | HLS9193 | Water | NA | NA | 6" | 8" | PRV | SA‐106 B | SA‐106 B | SA‐351 Gr CF8M | 600 | 455 | 41.4 | 235 | 600 | 150 | FL | FL |  | 901 | 62 | 9 & 1 | ‐ | Trillium | 2080_23207 | 23.03 | 4705 | 2080_00006‐1
D | 01‐LCV‐HLS901 | LP DRUM LEVEL CONTROL VALVE | HLS9118 | HLS9126 | Water | POVCTRL | FSC | 12" | 12" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 489 | 41.4 | 253.8 | 2500 | 2500 | BW | BW | EWT CAV III Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23416 | 23.04 | 4706 | 2080_00003‐1
D | 01‐PCV‐HLS901 | LP SPARGING STEAM CONTROL VALVE | HLS9130 | HLS9178 | Steam | POVCTRL | LSC | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 425 | 454 | 29.3 | 234.4 | 600 | 600 | SW | SW | ES Valve Body | 638 | 44 | 2 & 8 | ‐ | Fisher | 2080_23418 | 23.04 | 4707 | 2080_00003‐1
D | 01‐LCV‐HIS901 | IP DRUM LEVEL CONTROL VALVE | HIS9115 | HIS9116 | Water | POVCTRL | FSC | 3" | 3" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW | HPT Valve Body | 2100 | 145 | 3 | ‐ | Fisher | 2080_23407 | 23.04 | 4708 | 2080_00004‐2
D | 01‐PCV‐HIS901 | IP SPARGING STEAM CONTROL VALVE | HIS9141 | HIS9107 | Steam | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 656 | 498 | 45.2 | 259 | 600 | 600 | SW | SW | ES Valve Body | 935 | 65 | 4 | ‐ | Fisher | 2080_23410 | 23.04 | 4709 | 2080_00004‐2
D | 01‐PCV‐HIS902 | IP TO LP PEGGING STEAM CONTROL VALVE | HIS9202 | HIS9201 | Steam | POVCTRL | FSC | 3" | 3" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 502 | 43 | 261.1 | 600 | 600 | BW | BW | ET Valve Body | 935 | 65 | 2 & 4 | ‐ | Fisher | 2080_23406 | 23.04 | 4710 | 2080_00004‐2
D | 01‐PCV‐HIS903 | IP STEAM OUTLET BACK PRESSURE CONTROL VALVE | HIS9190 | HIS9148 | Steam | POVCTRL | FSO | 8" | 8" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 624 | 622 | 43 | 327.6 | 600 | 600 | BW | BW | ED Valve Body | 935 | 65 | 4 | ‐ | Fisher | 2080_23411 | 23.04 | 4711 | 2080_00004‐3
D | 01‐LCV‐HHS901 | HP DRUM LEVEL CONTROL VALVE 1 (25%‐100%) | HHS9103 | HHS9104 | Water | POVCTRL | FSC | 8" | 8" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | HPT Valve Body | 6150 | 424 | 6 | ‐ | Fisher | 2080_23401 | 23.04 | 4712 | 2080_00005‐1
D | 01‐LCV‐HHS902 | HP DRUM LEVEL CONTROL VALVE 2 (0‐30%) | HHS9107 | HHS9108 | Water | POVCTRL | FSC | 4" | 4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | HPT Valve Body | 6150 | 424 | 6 | ‐ | Fisher | 2080_23402 | 23.04 | 4713 | 2080_00005‐1
D | 01‐FCV‐HHS901 | HP SPARGING STEAM CONTROL VALVE | HHS9218 | HHS9221 | Steam | POVCTRL | FSC | 3" | 3" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2773 | 684 | 191.2 | 362.4 | 1500 | 1500 | BW | BW | HPD Valve Body | 4112 | 284 | 7 | ‐ | Fisher | 2080_23405 | 23.04 | 4714 | 2080_00005‐2
D | 01‐FCV‐HHS904 | HP TO IP CASCADING BLOWDOWN CONTROL VALVE | HHS9943 | HHS9944 | Water | NA | NA | 2" | 2" | Angle Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2773 | 684 | 191.2 | 362.4 | 1500 | 1500 | SW | SW | HPAS Valve Body | 4112 | 284 | 9 & 7 | ‐ | Fisher | 2080_23403 | 23.04 | 4715 | 2080_00005‐2
D | 01‐PCV‐HHS902 | HP STEAM OUTLET CONTROL VALVE | HHS9192 | HHS9192 | Steam | POVCTRL | FSC | 12" | 12" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐217 Gr C12A | 2534 | 1098 | 174.7 | 592 | 3200 | 3200 | BW | BW | HPD Valve Body | 4112 | 284 | 7 |  | Fisher | 2080_23421 | 23.04 | 4716 | 2080_00005‐3
D | 01‐TCV‐HLS901 | PREHEATER BYPASS CONTROL VALVE 1 | HLS9170 | HLS9171 | Water | POVCTRL | FSO | 10" | 10" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 345 | 41.4 | 174 | 600 | 600 | BW | BW | EWT Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23412 | 23.04 | 4717 | 2080_00006‐1
D | 01‐TCV‐HLS902 | PREHEATER BYPASS CONTROL VALVE 2 | HLS9117 | HLS9120 | Water | POVCTRL | FSO | 10" | 10" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 345 | 41.4 | 174 | 600 | 600 | BW | BW | EWT Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23413 | 23.04 | 4718 | 2080_00006‐1
D | 01‐TCV‐HLS903 | PREHEATER EXT HEAT EXCHANGER CONTROL VALVE 1 | HLS9121 | HLS9111 | Water | POVCTRL | FSO | 10" | 10" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 490 | 41.4 | 254.7 | 600 | 600 | BW | BW | EWT Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23414 | 23.04 | 4719 | 2080_00006‐1
D | 01‐TCV‐HLS904 | PREHEATER EXT HEAT EXCHANGER CONTROL VALVE 2 | HLS9122 | HLS9112 | Water | POVCTRL | FSO | 10" | 10" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 600 | 490 | 41.4 | 254.7 | 600 | 600 | BW | BW | EWT Valve Body | 901 | 62 | 1 | ‐ | Fisher | 2080_23415 | 23.04 | 4720 | 2080_00006‐1
D | 01‐FCV‐HIS904 | IP CONTINUOUS BLOWDOWN CONTROL VALVE | HIS9912 | HBD9108 | Water | NA | NA | 2" | 2" | Angle Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 656 | 498 | 45.2 | 259 | 600 | 600 | SW | SW | EAS Valve Body | 935 | 65 | 9 & 4 | ‐ | Fisher | 2080_23408 | 23.04 | 4721 | 2080_00007‐1
D | 01‐TCV‐HBD901 | BLOWDOWN TANK COOLING WATER CONTROL VALVE | HBD9109 | HBD9110 | Water | POVCTRL | FSC | 4" | 4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 58 | 750 | 4 | 399 | 600 | 600 | BW | BW | ET Valve Body | 78 | 5 | 9 | ‐ | Fisher | 2080_23419 | 23.04 | 4722 | 2080_00007‐1
D | 01‐YCV‐HHS901 | HP INTERMITTENT BLOWDOWN CONTROL VALVE | HHS9947 | HBD9905 | Water | POVCTRL | FSC | 2" | 2" | Angle Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 2998 | 696 | 206.7 | 368.9 | 1500 | 1500 | SW | SW | HPAS Valve Body | 4112 | 284 | 9 & 7 | ‐ | Fisher | 2080_23404 | 23.04 | 4723 | 2080_00007‐1
D | 01‐YCV‐HIS901 | IP INTERMITTENT BLOWDOWN CONTROL VALVE | HIS9917 | HBD9910 | Water | POVCTRL | FSC | 2" | 2" | Angle Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 812 | 522 | 56 | 272.2 | 600 | 600 | SW | SW | EAS Valve Body | 935 | 65 | 9 & 4 | ‐ | FIsher | 2080_23409 | 23.04 | 4724 | 2080_00007‐1
D | 01‐YCV‐HLS901 | LP INTERMITTENT BLOWDOWN CONTROL VALVE | HLS9934 | HBD9911 | Water | POVCTRL | FSC | 3" | 3" | Angle Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 196 | 386 | 13.5 | 196.5 | 600 | 600 | SW | SW | EAS Valve Body | 196 | 14 | 9 & 2 | ‐ | Fisher | 2080_23417 | 23.04 | 4725 | 2080_00007‐1
D | 01‐TCV‐HRS901 | REHEAT INTERSTAGE ATTEMPERATOR CONTROL VALVE | HRS9164 | HRS9164 | Water | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 1400 | 374 | 96.5 | 189.9 | 600 | 600 | BW | BW | ES Valve Body | 2100 | 145 | 3 | ‐ | Fisher | 2080_23506 | 23.05 | 4726 | 2080_00004‐4
D | 01‐TCV‐HRS902 | REHEAT FINAL ATTEMPERATOR CONTROL VALVE | BOP | BOP | Water | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 1400 | 374 | 96.5 | 189.9 | 600 | 600 | BW | BW | ET Valve Body | 2100 | 145 | 3 | ‐ | Fisher | 2080_23508 | 23.05 | 4727 | 2080_00004‐4
D | 01‐TCV‐HHS801 | HP INTERSTAGE ATTEMPERATOR CONTROL VALVE | HHS8199 | HHS8199 | Water | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | HPS Valve Body | 6150 | 424 | 6 | ‐ | Fisher | 2080_23502 | 23.05 | 4728 | 2080_00005‐3
D | 01‐TCV‐HHS902 | HP FINAL ATTEMPERATOR CONTROL VALVE | BOP | BOP | Water | POVCTRL | FSC | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCC | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | HPS Valve Body | 6150 | 424 | 6 | ‐ | Fisher | 2080_23504 | 23.05 | 4729 | 2080_00005‐3
D | 01‐VHEH910 | STACK DRAIN | HEH9906 | HEH9906 | Water | NA | NA | 3" | 3" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 15 | 212 | 1 | 100 | 150 | 150 | BW | BW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23008 | 23.21 | 4730 | 2080_00002‐1
D | 01‐VHLS924 | BFP SUCTION | HLS9149 | HLS9149 | Water | NA | NA | 12" | 12" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 162 | 372 | 11.2 | 188.7 | 150 | 150 | BW | BW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23007 | 23.21 | 4731 | 2080_00003‐1
D | 01‐VHLS940 | LP CV ISOLATION | HLS9118 | HLS9118 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 489 | 41.4 | 253.8 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23004 | 23.21 | 4732 | 2080_00003‐1
D | 01‐VHLS941 | LP CV ISOLATION | HLS9126 | HLS9127 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐217 Gr WC6 | 600 | 489 | 41.4 | 253.8 | 300 | 300 | BW | BW |  | 901 | 62 | 2 & 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23006 | 23.21 | 4733 | 2080_00003‐1
D | 01‐VHLS994 | LP STEAM SPARGING CHECK VALVE | HLS9178 | HLS9178 | Steam | NA | NA | 3" | 3" | Check Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCB | 162 | 372 | 11.2 | 188.7 | 300 | 300 | BW | BW | Previous tag 01‐VHLS944 (redundant with other valve) | 196 | 14 | 2 | ‐ | HP Valve | 2080_23002 | 23.21 | 4734 | 2080_00003‐1
D | 01‐VHIS901 | IP FEEDWATER INLET | HIS9100 | HIS9100 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 3 | Bypass Equalizer Type 1 | HP Valve | 2080_23025 | 23.21 | 4735 | 2080_00004‐1
D | 01‐VHIS902 | IP FEEDWATER INLET CHECK VALVE | HIS9106 | HIS9106 | Water | NA | NA | 4" | 4" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23029 | 23.21 | 4736 | 2080_00004‐1
D | 01‐VHIS921 | IP FGH EXTRACTION CHECK VALVE | HIS9114 | HIS9114 | Water | NA | NA | 4" | 4" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23021 | 23.21 | 4737 | 2080_00004‐1
D | 01‐VHIS934 | IP CV ISOLATION VALVE | HIS9113 | HIS9115 | Water | NA | NA | 4" | 4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 3 | Bypass Equalizer Type 1 | HP Valve | 2080_23015 | 23.21 | 4738 | 2080_00004‐2
D | 01‐VHIS935 | IP CV ISOLATION VALVE | HIS9116 | HIS9117 | Water | NA | NA | 4" | 4" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW |  | 2100 | 145 | 4 & 3 | Bypass Equalizer Type 4 | HP Valve | 2080_23016 | 23.21 | 4739 | 2080_00004‐2
D | 01‐VHIS975 | IP STEAM SPARGING CHECK VALVE | HIS9107 | HIS9107 | Steam | NA | NA | 3" | 3" | Check Valve | SA‐106 C | SA‐106 C | SA‐216 Gr WCB | 656 | 498 | 45.2 | 259 | 300 | 300 | BW | BW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23002 | 23.21 | 4740 | 2080_00004‐2
D | 01‐VHIS978 | IP PEGGING STEAM | HIS9212 | HIS9213 | Steam | NA | NA | 6" | 6" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐217 Gr WC6 | 131 | 365 | 9 | 184.9 | 300 | 300 | BW | BW |  | 196 | 14 | 2 | Bypass Equalizer Type 3 | HP Valve | 2080_23033 | 23.21 | 4741 | 2080_00004‐2
D | 01‐VHIS989 | IP NRV (STOP CHECK) | HIS9146 | HIS9147 | Steam | NA | NA | 8" | 8" | NRV (Stop‐Check) | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 624 | 622 | 43 | 327.6 | 300 SPL | 300 SPL | BW | BW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23003 | 23.21 | 4742 | 2080_00004‐3
D | 01‐VHRS830 | RH INTERSTAGE ATTEMPERATOR SPRAY WATER ISOLATION | HRS9182 | HRS9182 | Water | NA | NA | 2 1/2" | 2 1/2" | Gate Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW | Previously VHRS930 on P&ID | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23013 | 23.21 | 4743 | 2080_00004‐4
D | 01‐VHRS831 | RH INTERSTAGE ATTEMPERATOR SPRAY WATER SWING CHECK VALVE | HRS9182 | HRS9182 | Water | NA | NA | 2 1/2" | 2 1/2" | Check Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW | Previously VHRS931 on P&ID | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23018 | 23.21 | 4744 | 2080_00004‐4
D | 01‐VHHS901 | HP FEEDWATER CONTROL VALVE ISOLATION | HHS9102 | HHS9103 | Water | NA | NA | 12" | 12" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2000 | 2000 | BW | BW |  | 6150 | 424 | 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23024 | 23.21 | 4745 | 2080_00005‐1
D | 01‐VHHS902 | HP FEEDWATER CONTROL VALVE ISOLATION | HHS9104 | HHS9105 | Water | NA | NA | 12" | 12" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2000 | 2000 | BW | BW |  | 6150 | 424 | 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23024 | 23.21 | 4746 | 2080_00005‐1
D | 01‐VHHS903 | HP FEEDWATER CONTROL VALVE ISOLATION | HHS9106 | HHS9107 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW |  | 6150 | 424 | 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23026 | 23.21 | 4747 | 2080_00005‐1
D | 01‐VHHS904 | HP FEEDWATER CONTROL VALVE ISOLATION | HHS9108 | HHS9109 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW |  | 6150 | 424 | 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23026 | 23.21 | 4748 | 2080_00005‐1
D | 01‐VHHS911 | HP FEEDWATER INLET SWING CHECK VALVE | HHS9105 | HHS9105 | Water | NA | NA | 12" | 12" | Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2000 | 2000 | BW | BW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23017 | 23.21 | 4749 | 2080_00005‐1
D | 01‐VHHS948 | HP TCA RETURN TO HP ECONOMIZER ISOLATION | HHS9118 | HHS9118 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 4100 | 705 | 282.7 | 373.9 | 1500 SPL | 1500 SPL | BW | BW |  | 6150 | 424 | with BOP | Bypass Equalizer Type 1 | HP Valve | 2080_23035 | 23.21 | 4750 | 2080_00005‐1
D | 01‐VHHS949 | HP TCA RETURN TO HP ECONOMIZER CHECK | HHS9117 | HHS9118 | Water | NA | NA | 6" | 6" | Check Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 4100 | 705 | 282.7 | 373.9 | 1500 SPL | 1500 SPL | BW | BW |  | 6150 | 424 | with BOP | ‐ | HP Valve | 2080_23036 | 23.21 | 4751 | 2080_00005‐1
D | 01‐VHHS993 | HP STEAM SPARGING CHECK VALVE | HHS9221 | HHS9221 | Steam | NA | NA | 4" | 4" | Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 1500 SPL | 1500 SPL | BW | BW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23020 | 23.21 | 4752 | 2080_00005‐2
D | 01‐VHHS844 | HP INTERSTAGE ATTEMPERATOR SPRAY WATER ISOLATION | HHS8198 | HHS8200 | Water | NA | NA | 2 1/2" | 2 1/2" | Gate Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 4100 | 374 | 282.7 | 189.9 | 2500 LTD | 2500 LTD | BW | BW |  | 6150 | 424 | 7 & 6 | ‐ | HP Valve | 2080_23014 | 23.21 | 4753 | 2080_00005‐3
D | 01‐VHHS845 | HP INTERSTAGE ATTEMPERATOR SPRAY WATER SWING CHECK VALVE | HHS8200 | HHS8201 | Water | NA | NA | 2 1/2" | 2 1/2" | Check Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 4100 | 1032 | 282.7 | 555.6 | 2500 | 2500 | BW | BW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23019 | 23.21 | 4754 | 2080_00005‐3
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 4755 | 2080_00003‐1
D | 01‐VHLS901 | LP FEEDWATER INLET CHECK | HLS9101 | HLS9102 | Water | NA | NA | 10" | 10" | Check Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23001 | 23.21 | 4756 | 2080_00006‐1
D | 01‐VHLS904 | LP HEAT EXCHANGER ISOLATION | HLS9171 | HLS9174 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 | 300 | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23005 | 23.21 | 4757 | 2080_00006‐1
D | 01‐VHLS905 | LP HEAT EXCHANGER ISOLATION | HLS9111 | HLS9179 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 490 | 41.4 | 254.7 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23004 | 23.21 | 4758 | 2080_00006‐1
D | 01‐VHLS907 | LP HEAT EXCHANGER ISOLATION | HLS9104 | HLS9105 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23004 | 23.21 | 4759 | 2080_00006‐1
D | 01‐VHLS908 | LP HEAT EXCHANGER ISOLATION | HLS9113 | HLS9123 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 490 | 41.4 | 254.7 | 300 SPL | 300 SPL | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23004 | 23.21 | 4760 | 2080_00006‐1
D | 01‐VHLS909 | LP HEAT EXCHANGER BYPASS | HLS9114 | HLS9172 | Water | NA | NA | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 | 300 | BW | BW |  | 901 | 62 | 1 | Bypass Equalizer Type 3 | HP Valve | 2080_23034 | 23.21 | 4761 | 2080_00006‐1
D | 01‐VHBD904 | BLOW DOWN TANK CV ISOLATION | HBD9109 | HBD9109 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 1500 | 1500 | BW | BW |  | 78 | 5 | 9 | Bypass Equalizer Type 4 | HP Valve | 2080_23031 | 23.21 | 4762 | 2080_00007‐1
D | 01‐VHBD905 | BLOW DOWN TANK CV ISOLATION | HBD9110 | HBD9110 | Water | NA | NA | 6" | 6" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 1500 | 1500 | BW | BW |  | 78 | 5 | 9 | Bypass Equalizer Type 4 | HP Valve | 2080_23031 | 23.21 | 4763 | 2080_00007‐1
D | 01‐VHBD906 | BLOW DOWN TANK CHECK | HBD9110 | HBD9110 | Water | NA | NA | 6" | 6" | Check Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 58 | 750 | 4 | 399 | 150 | 150 | BW | BW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23032 | 23.21 | 4764 | 2080_00007‐1
D | 01‐VHEH901 | EXHAUST SIDE INLET DUCT PRESSURE TRANSMITTER ISOLATION | HEH9801 | HEH9801 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1100 | 0.1 | 593.3 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4765 | 2080_00002‐1
D | 01‐VHEH902 | EXHAUST SIDE INLET DUCT PRESSURE TRANSMITTER ISOLATION | HEH9802 | HEH9802 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1100 | 0.1 | 593.3 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4766 | 2080_00002‐1
D | 01‐VHEH903 | EXHAUST SIDE INLET DUCT PRESSURE TRANSMITTER ISOLATION | HEH9803 | HEH9803 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1100 | 0.1 | 593.3 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4767 | 2080_00002‐1
D | 01‐VHEH904 | EXHAUST SIDE CO CATALYST 1 PRESSURE TRASMITTER ISOLATION | HEH9804 | HEH9804 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1033 | 0.1 | 556.1 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4768 | 2080_00002‐1
D | 01‐VHEH905 | EXHAUST SIDE CO CATALYST 1 PRESSURE TRASMITTER ISOLATION | HEH9805 | HEH9805 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F12 | 1 | 1033 | 0.1 | 556.1 | 1500 | 1500 | SW | SW |  | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23117 | 23.22 | 4769 | 2080_00002‐1
D | 01‐VHEH906 | EXHAUST SIDE CO CATALYST 2 PRESSURE TRASMITTER ISOLATION | HEH9806 | HEH9806 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1 | 566 | 0.1 | 296.7 | 800 | 800 | SW | SW | SPARE 01‐VHIS954 on valve drawing 2080_23126 Rev D | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23126 | 23.22 | 4770 | 2080_00002‐1
D | 01‐VHEH907 | EXHAUST SIDE CO CATALYST 2 PRESSURE TRASMITTER ISOLATION | HEH9807 | HEH9807 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1 | 566 | 0.1 | 296.7 | 800 | 800 | SW | SW | SPARE 01‐VHIS955 on valve drawing 2080_23126 Rev D | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23126 | 23.22 | 4771 | 2080_00002‐1
D | 01‐VHEH908 | EXHAUST SIDE SCR CATALYST PRESSURE TRASMITTER ISOLATION | HEH9808 | HEH9808 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1 | 566 | 0.1 | 296.7 | 800 | 800 | SW | SW | SPARE 01‐VHIS956 on valve drawing 2080_23126 Rev D | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23126 | 23.22 | 4772 | 2080_00002‐1
D | 01‐VHEH909 | EXHAUST SIDE SCR CATALYST PRESSURE TRASMITTER ISOLATION | HEH9809 | HEH9809 | Flue gas | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1 | 566 | 0.1 | 296.7 | 800 | 800 | SW | SW | SPARE 01‐VHIS957 on valve drawing 2080_23126 Rev D | N.A. | N.A. | ‐ | ‐ | HP Valve | 2080_23126 | 23.22 | 4773 | 2080_00002‐1
D | 01‐VHEH912 | BURNER MAIN FUEL LINE DRAIN | BUR9901 | BUR9901 | Nat. Gas | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 100 | 130 | 6.9 | 54.4 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS985 on valve drawing 2080_23106 Rev D | N.A. | N.A. | ‐ |  | HP Valve | 2080_23106 | 23.22 | 4774 | 2080_00002‐1
D | 01‐VHEH913 | BURNER PILOT FUEL LINE DRAIN | BUR9902 | BUR9902 | Nat. Gas | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 100 | 130 | 6.9 | 54.4 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS986 on valve drawing 2080_23106 Rev D | N.A. | N.A. | ‐ |  | HP Valve | 2080_23106 | 23.22 | 4775 | 2080_00002‐1
D | 01‐VHEH914 | BURNER INSTRUMENT AIR DRAIN | BUR9903 | BUR9903 | Air | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 150 | 130 | 10.3 | 54.4 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS865 on valve drawing 2080_23106 Rev D | N.A. | N.A. | ‐ |  | HP Valve | 2080_23106 | 23.22 | 4776 | 2080_00002‐1
D | 01‐VHEH915 | BURNER COOLING AIR DRAIN | BUR9904 | BUR9904 | Air | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 20 | 110 | 1.4 | 43.3 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS907 on valve drawing 2080_23106 Rev D | N.A. | N.A. | ‐ |  | HP Valve | 2080_23106 | 23.22 | 4777 | 2080_00002‐1
D | 01‐VHLS805 | LP SATURATED STEAM VENT | HLS9992 | HLS9992 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4778 | 2080_00003‐1
D | 01‐VHLS806 | LP SATURATED STEAM VENT | HLS9992 | HLS9992 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4779 | 2080_00003‐1
D | 01‐VHLS831 | DEAERATOR VENT ISOLATION VALVE | HLS9975 | HLS9975 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | SPARE 01‐VHIS940 on valve drawing ("Spare 26" on 23E21 Rev C) | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4780 | 2080_00003‐1
D | 01‐VHLS832 | DEAERATOR VENT ISOLATION VALVE | HLS9977 | HLS9977 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | SPARE 01‐VHIS943 on valve drawing ("Spare 27" on 23E21 Rev C) | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4781 | 2080_00003‐1
D | 01‐VHLS833 | DEAERATOR VENT ISOLATION VALVE | HLS9975 | HLS9975 | Water | NA | NA | 2" | 2" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | New on Rev. D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23128 | 23.22 | 4782 | 2080_00003‐1
D | 01‐VHLS834 | DEAERATOR VENT ISOLATION VALVE | HLS9977 | HLS9977 | Water | NA | NA | 2" | 2" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | New on Rev. D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23128 | 23.22 | 4783 | 2080_00003‐1
D | 01‐VHLS923 | PREHEATER DRAIN | HLS9990 | HLS9990 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4784 | 2080_00003‐1
D | 01‐VHLS925 | PREHEATER DRAIN | HLS9990 | HLS9940 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4785 | 2080_00003‐1
D | 01‐VHLS926 | PREHEATER OUTLET PRESSURE INDICATOR ISOLATION | HLS9840 | HLS9840 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 2500 | 2500 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23109 | 23.22 | 4786 | 2080_00003‐1
D | 01‐VHLS927 | PREHEATER OUTLET PRESSURE INDICATOR ISOLATION | HLS9840 | HLS9840 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 2500 | 2500 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23109 | 23.22 | 4787 | 2080_00003‐1
D | 01‐VHLS930 | PREHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HLS9802 | HLS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4788 | 2080_00003‐1
D | 01‐VHLS931 | PREHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HLS9802 | HLS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4789 | 2080_00003‐1
D | 01‐VHLS932 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9803 | HLS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4790 | 2080_00003‐1
D | 01‐VHLS933 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9803 | HLS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4791 | 2080_00003‐1
D | 01‐VHLS934 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9804 | HLS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4792 | 2080_00003‐1
D | 01‐VHLS935 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9804 | HLS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4793 | 2080_00003‐1
D | 01‐VHLS936 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9805 | HLS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4794 | 2080_00003‐1
D | 01‐VHLS937 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9805 | HLS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4795 | 2080_00003‐1
D | 01‐VHLS938 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9806 | HLS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4796 | 2080_00003‐1
D | 01‐VHLS939 | PREHEATER OUTLET FLOW TRANSMITTER ISOLATION | HLS9806 | HLS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 4797 | 2080_00003‐1
D | 01‐VHLS942 | LP DRUM LCV BYPASS | HLS9128 | HLS9129 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 2 & 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 4798 | 2080_00003‐1
D | 01‐VHLS943 | PREHEATER OUTLET DRAIN (DOWNSTREAM LCV) | HLS9916 | HLS9916 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23124 | 23.22 | 4799 | 2080_00003‐1
D | 01‐VHLS944 | PREHEATER OUTLET DRAIN (DOWNSTREAM LCV) | HLS9916 | HLS9917 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23124 | 23.22 | 4800 | 2080_00003‐1
D | 01‐VHLS945 | LP DRUM DEAERATOR PRESSURE INDICATOR ISOLATION | HLS9807 | HLS9807 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4801 | 2080_00003‐1
D | 01‐VHLS946 | LP DRUM DEAERATOR PRESSURE INDICATOR ISOLATION | HLS9807 | HLS9807 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4802 | 2080_00003‐1
D | 01‐VHLS947 | LP DRUM DEAERATOR VENT | HLS9975 | HLS9975 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4803 | 2080_00003‐1
D | 01‐VHLS948 | LP DRUM DEAERATOR VENT | HLS9977 | HLS9977 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4804 | 2080_00003‐1
D | 01‐VHLS949 | LP DRUM LEVEL GAUGE ISOLATION | HLS9814 | HLS9814 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4805 | 2080_00003‐1
D | 01‐VHLS950 | LP DRUM LEVEL INDICATION DRAIN | HLS9918 | HLS9918 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4806 | 2080_00003‐1
D | 01‐VHLS951 | LP DRUM LEVEL INDICATION DRAIN | HLS9919 | HLS9920 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4807 | 2080_00003‐1
D | 01‐VHLS952 | LP DRUM LEVEL INDICATION DRAIN | HLS9919 | HLS9919 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4808 | 2080_00003‐1
D | 01‐VHLS953 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9811 | HLS9811 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4809 | 2080_00003‐1
D | 01‐VHLS954 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9811 | HLS9811 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4810 | 2080_00003‐1
D | 01‐VHLS955 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9813 | HLS9813 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4811 | 2080_00003‐1
D | 01‐VHLS956 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9813 | HLS9813 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4812 | 2080_00003‐1
D | 01‐VHLS957 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9808 | HLS9808 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4813 | 2080_00003‐1
D | 01‐VHLS958 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9808 | HLS9808 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4814 | 2080_00003‐1
D | 01‐VHLS959 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9810 | HLS9810 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4815 | 2080_00003‐1
D | 01‐VHLS960 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9810 | HLS9810 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4816 | 2080_00003‐1
D | 01‐VHLS961 | LP DRUM LEVEL GAUGE ISOLATION | HLS9814 | HLS9815 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4817 | 2080_00003‐1
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 4818 | 2080_00003‐1
D | 01‐VHLS962 | LP DRUM LEVEL GAUGE ISOLATION | HLS9816 | HLS9817 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4819 | 2080_00003‐1
D | 01‐VHLS963 | LP DRUM LEVEL GAUGE ISOLATION | HLS9816 | HLS9816 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4820 | 2080_00003‐1
D | 01‐VHLS964 | LP DRUM LEVEL GAUGE ISOLATION | HLS9821 | HLS9821 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4821 | 2080_00003‐1
D | 01‐VHLS965 | LP DRUM LEVEL GAUGE ISOLATION | HLS9821 | HLS9822 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4822 | 2080_00003‐1
D | 01‐VHLS966 | LP DRUM LEVEL INDICATION DRAIN | HLS9925 | HLS9926 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4823 | 2080_00003‐1
D | 01‐VHLS967 | LP DRUM LEVEL INDICATION DRAIN | HLS9925 | HLS9925 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4824 | 2080_00003‐1
D | 01‐VHLS968 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9820 | HLS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4825 | 2080_00003‐1
D | 01‐VHLS969 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9820 | HLS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4826 | 2080_00003‐1
D | 01‐VHLS970 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9818 | HLS9818 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4827 | 2080_00003‐1
D | 01‐VHLS971 | LP DRUM LEVEL TRANSMITTER ISOLATION | HLS9818 | HLS9818 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23131 | 23.22 | 4828 | 2080_00003‐1
D | 01‐VHLS972 | LP DRUM LEVEL GAUGE ISOLATION | HLS9823 | HLS9824 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4829 | 2080_00003‐1
D | 01‐VHLS973 | LP DRUM LEVEL GAUGE ISOLATION | HLS9823 | HLS9823 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23103 | 23.22 | 4830 | 2080_00003‐1
D | 01‐VHLS974 | LP DRUM NITROGEN ISOLATION | HRG9105 | HLS9404 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 4831 | 2080_00003‐1
D | 01‐VHLS975 | LP DRUM NITROGEN SUPPLY NRV | HLS9404 | HLS9404 | Water/Steam | NA | NA | 2" | 2" | Stop Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 1500 | 1500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23102 | 23.22 | 4832 | 2080_00003‐1
D | 01‐VHLS976 | LP DRUM PRESSURE INDICATOR ISOLATION | HLS9825 | HLS9825 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4833 | 2080_00003‐1
D | 01‐VHLS977 | LP DRUM PRESSURE INDICATOR ISOLATION | HLS9825 | HLS9825 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4834 | 2080_00003‐1
D | 01‐VHLS978 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9826 | HLS9826 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4835 | 2080_00003‐1
D | 01‐VHLS979 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9826 | HLS9826 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4836 | 2080_00003‐1
D | 01‐VHLS980 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9827 | HLS9827 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4837 | 2080_00003‐1
D | 01‐VHLS981 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9827 | HLS9827 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4838 | 2080_00003‐1
D | 01‐VHLS982 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9828 | HLS9828 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4839 | 2080_00003‐1
D | 01‐VHLS983 | LP DRUM PRESSURE TRANSMITTER ISOLATION | HLS9828 | HLS9828 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4840 | 2080_00003‐1
D | 01‐VHLS985 | LP SPARGING STEAM DRAIN | HLS9923 | HLS9923 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 425 | 454 | 29.3 | 234.4 | 2500 | 2500 | SW | SW | SPARE_297 on valve drawing 2080_23113 Rev D | 638 | 44 | 8 | ‐ | HP Valve | 2080_23113 | 23.22 | 4841 | 2080_00003‐1
D | 01‐VHLS988 | LP ECONOMIZER OUTLET VENT | HLS9976 | HLS9976 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | SPARE 01‐VHIS993 on valve drawing 2080_23120 Rev D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4842 | 2080_00003‐1
D | 01‐VHLS989 | LP ECONOMIZER OUTLET VENT | HLS9976 | HLS9976 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 356 | 9 | 179.9 | 800 | 800 | SW | SW | SPARE 01‐VHIS936 on valve drawing 2080_23120 Rev D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4843 | 2080_00003‐1
D | 01‐VHLS990 | LP DRUM WATER SAMPLE ISOLATION | HLS9606 | HLS9606 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 162 | 372 | 11.2 | 188.7 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4844 | 2080_00003‐1
D | 01‐VHLS991 | LP DRUM WATER SAMPLE ISOLATION | HLS9606 | HLS9606 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 162 | 372 | 11.2 | 188.7 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4845 | 2080_00003‐1
D | 01‐VHLS992 | LP SPARGING STEAM STRAIN DRAIN | HLS9921 | HLS9921 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 162 | 372 | 11.2 | 188.7 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23113 | 23.22 | 4846 | 2080_00003‐1
D | 01‐VHLS993 | LP SPARGING STEAM STRAIN DRAIN | HLS9921 | HLS9922 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 162 | 372 | 11.2 | 188.7 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23113 | 23.22 | 4847 | 2080_00003‐1
D | 01‐VHLS997 | PREHEATER OUTLET DRAIN | HLS9301 | HLS9301 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4848 | 2080_00003‐1
D | 01‐VHLS998 | PREHEATER OUTLET DRAIN | HLS9301 | HLS9302 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 4849 | 2080_00003‐1
D | 01‐VHLS999 | LP SPARGING STEAM DRAIN | HLS9923 | HLS9924 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 425 | 454 | 29.3 | 234.4 | 2500 | 2500 | SW | SW | SPARE_428 on valve drawing 2080_23113 Rev D | 638 | 44 | 8 | ‐ | HP Valve | 2080_23113 | 23.22 | 4850 | 2080_00003‐1
D | 01‐VHLS808 | LP SUPERHEATED STEAM SAMPLE ISOLATION | HLS8610 | HLS8610 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 131 | 623 | 9 | 328.5 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23108 | 23.22 | 4851 | 2080_00003‐2
D | 01‐VHLS809 | LP SUPERHEATED STEAM SAMPLE ISOLATION | HLS8610 | HLS8610 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 131 | 623 | 9 | 328.5 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23108 | 23.22 | 4852 | 2080_00003‐2
D | 01‐VHLS811 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9841 | HLS9841 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4853 | 2080_00003‐2
D | 01‐VHLS812 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9841 | HLS9841 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4854 | 2080_00003‐2
D | 01‐VHLS813 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9842 | HLS9842 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4855 | 2080_00003‐2
D | 01‐VHLS814 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9842 | HLS9842 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4856 | 2080_00003‐2
D | 01‐VHLS815 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9843 | HLS9843 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4857 | 2080_00003‐2
D | 01‐VHLS816 | LP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HLS9843 | HLS9843 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4858 | 2080_00003‐2
D | 01‐VHLS817 | LP SUPERHEATED STEAM PRESSURE INDICATOR ISOLATION | HLS9844 | HLS9844 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4859 | 2080_00003‐2
D | 01‐VHLS818 | LP SUPERHEATED STEAM PRESSURE INDICATOR ISOLATION | HLS9844 | HLS9844 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4860 | 2080_00003‐2
D | 01‐VHLS819 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8809 | HLS8809 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4861 | 2080_00003‐2
D | 01‐VHLS820 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8809 | HLS8809 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4862 | 2080_00003‐2
D | 01‐VHLS821 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8807 | HLS8807 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4863 | 2080_00003‐2
D | 01‐VHLS822 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8807 | HLS8807 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23123 | 23.22 | 4864 | 2080_00003‐2
D | 01‐VHLS825 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8805 | HLS8805 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23109 | 23.22 | 4865 | 2080_00003‐2
D | 01‐VHLS826 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8805 | HLS8805 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 2500 | 2500 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23109 | 23.22 | 4866 | 2080_00003‐2
D | 01‐VHLS827 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8803 | HLS8803 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW | 01‐VHEH906 on valve drawing 2080_23127 Rev B | 196 | 14 | 2 | ‐ | HP Valve | 2080_23127 | 23.22 | 4867 | 2080_00003‐2
D | 01‐VHLS828 | LP SUPERHEATED STEAM FLOW TRANSMITTER ISOLATION | HLS8803 | HLS8803 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 623 | 9 | 328.5 | 800 | 800 | SW | SW | 01‐VHEH908 on valve drawing 2080_23127 Rev B | 196 | 14 | 2 | ‐ | HP Valve | 2080_23127 | 23.22 | 4868 | 2080_00003‐2
D | 01‐VHLS986 | LP SUPERHEATER OUTLET DRAIN POT CLEANOUT DRAIN | HLS9303 | HLS9303 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 624 | 9 | 328.7 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23126 | 23.22 | 4869 | 2080_00003‐2
D | 01‐VHLS987 | LP SUPERHEATER OUTLET DRAIN POT CLEANOUT DRAIN | HLS9303 | HLS9304 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 624 | 9 | 328.7 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23126 | 23.22 | 4870 | 2080_00003‐2
D | 01‐VHIS904 | IP FEEDWATER BOILER FILL ISOLATION | HIS9108 | HIS9134 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4871 | 2080_00004‐1
D | 01‐VHIS905 | IP FEEDWATER BOILER FILL CHECK VALVE | HIS9134 | HIS9109 | Water | NA | NA | 2" | 2" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23128 | 23.22 | 4872 | 2080_00004‐1
D | 01‐VHIS906 | IP FEEDWATER PRESSURE TRANSMITTER ISOLATION | HIS9801 | HIS9801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4873 | 2080_00004‐1
D | 01‐VHIS907 | IP FEEDWATER PRESSURE TRANSMITTER ISOLATION | HIS9801 | HIS9801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4874 | 2080_00004‐1
D | 01‐VHIS910 | IP ECONOMIZER INLET DRAIN | HIS9903 | HIS9903 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4875 | 2080_00004‐1
D | 01‐VHIS911 | IP ECONOMIZER DRAIN | HIS9904 | HIS9308 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.6 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4876 | 2080_00004‐1
D | 01‐VHIS912 | IP ECONOMIZER DRAIN | HIS9905 | HIS9309 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4877 | 2080_00004‐1
D | 01‐VHIS913 | IP ECONOMIZER DRAIN | HIS9309 | HIS9906 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 9 & 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4878 | 2080_00004‐1
D | 01‐VHIS915 | IP ECONOMIZER VENT | HIS9952 | HIS9353 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.6 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4879 | 2080_00004‐1
D | 01‐VHIS917 | IP ECONOMIZER VENT | HIS9954 | HIS9358 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4880 | 2080_00004‐1
D | 01‐VHIS918 | IP ECONOMIZER VENT | HIS9978 | HIS9978 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4881 | 2080_00004‐1
D | 01‐VHIS919 | IP FEEDWATER DRAIN | HIS9901 | HIS9901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4882 | 2080_00004‐1
D | 01‐VHIS920 | IP FEEDWATER DRAIN | HIS9901 | HIS9902 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4883 | 2080_00004‐1
D | 01‐VHIS846 | IP SATURATED STEAM VENT | HIS9957 | HIS9957 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23106 | 23.22 | 4884 | 2080_00004‐2
D | 01‐VHIS847 | IP SATURATED STEAM VENT | HIS9957 | HIS9957 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23106 | 23.22 | 4885 | 2080_00004‐2
D | 01‐VHIS848 | IP SATURATED STEAM VENT | HIS9958 | HIS9958 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23106 | 23.22 | 4886 | 2080_00004‐2
D | 01‐VHIS849 | IP SATURATED STEAM VENT | HIS9958 | HIS9958 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23106 | 23.22 | 4887 | 2080_00004‐2
D | 01‐VHIS850 | IP SATURATED STEAM VENT | HIS9959 | HIS9959 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23120 | 23.22 | 4888 | 2080_00004‐2
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 4889 | 2080_00003‐1
D | 01‐VHIS851 | IP SATURATED STEAM VENT | HIS9959 | HIS9959 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23120 | 23.22 | 4890 | 2080_00004‐2
D | 01‐VHIS852 | IP SPARGING STEAM STRAIN DRAIN | HIS8306 | HIS8306 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 656 | 498 | 45.2 | 259 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23113 | 23.22 | 4891 | 2080_00004‐2
D | 01‐VHIS853 | IP SPARGING STEAM STRAIN DRAIN | HIS8306 | HIS8307 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 656 | 498 | 45.2 | 259 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23113 | 23.22 | 4892 | 2080_00004‐2
D | 01‐VHIS854 | IP ECONOMIZER OUTLET DRAIN | HIS8310 | HIS8310 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4893 | 2080_00004‐2
D | 01‐VHIS855 | IP ECONOMIZER OUTLET DRAIN | HIS8310 | HIS8311 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4894 | 2080_00004‐2
D | 01‐VHIS860 | IP SPARGING STEAM DRAIN | HIS8308 | HIS8308 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 656 | 498 | 45.2 | 259 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS963 on valve drawing 2080_23113 Rev D | 935 | 65 | 4 | ‐ | HP Valve | 2080_23113 | 23.22 | 4895 | 2080_00004‐2
D | 01‐VHIS861 | IP SPARGING STEAM DRAIN | HIS8308 | HIS8309 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 656 | 498 | 45.2 | 259 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS964 on valve drawing 2080_23113 Rev D | 935 | 65 | 4 | ‐ | HP Valve | 2080_23113 | 23.22 | 4896 | 2080_00004‐2
D | 01‐VHIS914 | IP FEEDWATER PRESSURE INDICATOR ISOLATION | HIS9853 | HIS9853 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 2500 | 2500 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4897 | 2080_00004‐2
D | 01‐VHIS916 | IP FEEDWATER PRESSURE INDICATOR ISOLATION | HIS9853 | HIS9853 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 2500 | 2500 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4898 | 2080_00004‐2
D | 01‐VHIS922 | IP ECONOMIZER OUTLET PRESSURE TRANSMITTER ISOLATION | HIS9802 | HIS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4899 | 2080_00004‐2
D | 01‐VHIS923 | IP ECONOMIZER OUTLET PRESSURE TRANSMITTER ISOLATION | HIS9802 | HIS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4900 | 2080_00004‐2
D | 01‐VHIS924 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9803 | HIS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4901 | 2080_00004‐2
D | 01‐VHIS925 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9803 | HIS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4902 | 2080_00004‐2
D | 01‐VHIS926 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9804 | HIS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4903 | 2080_00004‐2
D | 01‐VHIS927 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9804 | HIS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4904 | 2080_00004‐2
D | 01‐VHIS928 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9805 | HIS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4905 | 2080_00004‐2
D | 01‐VHIS929 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9805 | HIS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4906 | 2080_00004‐2
D | 01‐VHIS930 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9806 | HIS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4907 | 2080_00004‐2
D | 01‐VHIS931 | IP ECONOMIZER OUTLET FLOW TRANSMITTER ISOLATION | HIS9806 | HIS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4908 | 2080_00004‐2
D | 01‐VHIS932 | IP ECONOMIZER OUTLET DRAIN | HIS9908 | HIS9908 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4909 | 2080_00004‐2
D | 01‐VHIS933 | IP ECONOMIZER OUTLET DRAIN | HIS9908 | HIS9909 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 4910 | 2080_00004‐2
D | 01‐VHIS936 | IP DRUM LCV BYPASS | HIS9118 | HIS9119 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 800 | 800 | SW | SW |  | 2100 | 145 | 4 & 3 | ‐ | HP Valve | 2080_23120 | 23.22 | 4911 | 2080_00004‐2
D | 01‐VHIS937 | IP ECONOMIZER OUTLET DRAIN (DOWNSTREAM LCV) | HIS9910 | HIS9910 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23124 | 23.22 | 4912 | 2080_00004‐2
D | 01‐VHIS938 | IP ECONOMIZER OUTLET DRAIN (DOWNSTREAM LCV) | HIS9910 | HIS9911 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23124 | 23.22 | 4913 | 2080_00004‐2
D | 01‐VHIS939 | IP DRUM LEVEL GAUGE ISOLATION | HIS9807 | HIS9807 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4914 | 2080_00004‐2
D | 01‐VHIS940 | IP DRUM LEVEL GAUGE ISOLATION | HIS9807 | HIS9807 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4915 | 2080_00004‐2
D | 01‐VHIS941 | IP DRUM LEVEL GAUGE DRAIN | HIS9907 | HIS9920 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4916 | 2080_00004‐2
D | 01‐VHIS942 | IP DRUM LEVEL GAUGE DRAIN | HIS9907 | HIS9907 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4917 | 2080_00004‐2
D | 01‐VHIS943 | IP DRUM LEVEL GAUGE ISOLATION | HIS9810 | HIS9810 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4918 | 2080_00004‐2
D | 01‐VHIS944 | IP DRUM LEVEL GAUGE DRAIN | HIS9919 | HIS9919 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4919 | 2080_00004‐2
D | 01‐VHIS945 | IP DRUM LEVEL GAUGE DRAIN | HIS9918 | HIS9928 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4920 | 2080_00004‐2
D | 01‐VHIS946 | IP DRUM LEVEL GAUGE DRAIN | HIS9918 | HIS9918 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4921 | 2080_00004‐2
D | 01‐VHIS947 | IP DRUM LEVEL GAUGE ISOLATION | HIS9812 | HIS9813 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4922 | 2080_00004‐2
D | 01‐VHIS948 | IP DRUM LEVEL GAUGE ISOLATION | HIS9810 | HIS9811 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4923 | 2080_00004‐2
D | 01‐VHIS949 | IP DRUM LEVEL GAUGE ISOLATION | HIS9812 | HIS9812 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4924 | 2080_00004‐2
D | 01‐VHIS950 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9814 | HIS9814 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4925 | 2080_00004‐2
D | 01‐VHIS951 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9814 | HIS9814 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4926 | 2080_00004‐2
D | 01‐VHIS952 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9816 | HIS9816 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4927 | 2080_00004‐2
D | 01‐VHIS953 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9816 | HIS9816 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4928 | 2080_00004‐2
D | 01‐VHIS954 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9817 | HIS9817 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4929 | 2080_00004‐2
D | 01‐VHIS955 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9817 | HIS9817 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4930 | 2080_00004‐2
D | 01‐VHIS956 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9819 | HIS9819 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4931 | 2080_00004‐2
D | 01‐VHIS957 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9819 | HIS9819 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4932 | 2080_00004‐2
D | 01‐VHIS958 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9820 | HIS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4933 | 2080_00004‐2
D | 01‐VHIS959 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9820 | HIS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4934 | 2080_00004‐2
D | 01‐VHIS960 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9822 | HIS9822 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4935 | 2080_00004‐2
D | 01‐VHIS961 | IP DRUM LEVEL TRANSMITTER ISOLATION | HIS9822 | HIS9822 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23131 | 23.22 | 4936 | 2080_00004‐2
D | 01‐VHIS963 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9823 | HIS9823 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4937 | 2080_00004‐2
D | 01‐VHIS964 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9823 | HIS9823 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4938 | 2080_00004‐2
D | 01‐VHIS965 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9824 | HIS9824 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4939 | 2080_00004‐2
D | 01‐VHIS966 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9824 | HIS9824 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4940 | 2080_00004‐2
D | 01‐VHIS967 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9825 | HIS9825 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4941 | 2080_00004‐2
D | 01‐VHIS968 | IP DRUM PRESSURE TRANSMITTER ISOLATION | HIS9825 | HIS9825 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4942 | 2080_00004‐2
D | 01‐VHIS969 | IP DRUM PRESSURE INDICATOR ISOLATION | HIS9826 | HIS9826 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4943 | 2080_00004‐2
D | 01‐VHIS970 | IP DRUM PRESSURE INDICATOR ISOLATION | HIS9826 | HIS9826 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4944 | 2080_00004‐2
D | 01‐VHIS971 | IP DRUM NITROGEN SUPPLY ISOLATION | HRG9104 | HIS9404 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 4945 | 2080_00004‐2
D | 01‐VHIS972 | IP DRUM NITROGEN SUPPLY NRV | HIS9404 | HIS9404 | Water/Steam | NA | NA | 2" | 2" | Stop Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 1500 | 1500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23102 | 23.22 | 4946 | 2080_00004‐2
D | 01‐VHIS973 | IP DRUM WATER SAMPLE ISOLATION | HIS9602 | HIS9602 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4947 | 2080_00004‐2
D | 01‐VHIS974 | IP DRUM WATER SAMPLE ISOLATION | HIS9602 | HIS9602 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4948 | 2080_00004‐2
D | 01‐VHIS976 | IP SATURATED STEAM VENT | HIS9960 | HIS9960 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23120 | 23.22 | 4949 | 2080_00004‐2
D | 01‐VHIS977 | IP SATURATED STEAM VENT | HIS9960 | HIS9960 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23120 | 23.22 | 4950 | 2080_00004‐2
D | 01‐VHIS979 | IP DRUM LEVEL GAUGE ISOLATION | HIS9809 | HIS9809 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4951 | 2080_00004‐2
D | 01‐VHIS991 | IP DRUM INLET CHEMICAL INJECTION CHECK VALVE | HIS9504 | HIS9504 | Water | NA | NA | 1" | 1" | Check Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23129 | 23.22 | 4952 | 2080_00004‐2
D | 01‐VHIS992 | IP DRUM INLET CHEMICAL INJECTION ISOLATION | HIS9504 | HIS9504 | Water | NA | NA | 1" | 1" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23121 | 23.22 | 4953 | 2080_00004‐2
D | 01‐VHIS993 | IP DRUM LEVEL GAUGE ISOLATION | HIS9809 | HIS9809 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 493 | 43 | 256.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4954 | 2080_00004‐2
D | 01‐VHIS998 | IP TO LP PEGGING STEAM VENT | HIS9979 | HIS9979 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 365 | 9 | 184.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4955 | 2080_00004‐2
D | 01‐VHIS999 | IP TO LP PEGGING STEAM VENT | HIS9979 | HIS9979 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 365 | 9 | 184.9 | 800 | 800 | SW | SW |  | 196 | 14 | 2 | ‐ | HP Valve | 2080_23120 | 23.22 | 4956 | 2080_00004‐2
D | 01‐VHIS801 | IP SUPERHEATED STEAM DRAIN | HIS9930 | HIS9930 | Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4957 | 2080_00004‐3
D | 01‐VHIS802 | IP SUPERHEATED STEAM DRAIN | HIS9930 | HIS9930 | Steam | NA | NA | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23103 | 23.22 | 4958 | 2080_00004‐3
D | 01‐VHIS856 | IP SUPERHEATER OUTLET DRAIN POT CLEANOUT DRAIN | HIS8313 | HIS8313 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23126 | 23.22 | 4959 | 2080_00004‐3
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 4960 | 2080_00003‐1
D | 01‐VHIS857 | IP SUPERHEATER OUTLET DRAIN POT CLEANOUT DRAIN | HIS8313 | HIS8314 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23126 | 23.22 | 4961 | 2080_00004‐3
D | 01‐VHIS858 | IP STEAM OUTLET DRAIN POT CLEANOUT DRAIN | HIS8312 | HIS8312 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23126 | 23.22 | 4962 | 2080_00004‐3
D | 01‐VHIS859 | IP STEAM OUTLET DRAIN POT CLEANOUT DRAIN | HIS8312 | HIS8315 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23126 | 23.22 | 4963 | 2080_00004‐3
D | 01‐VHIS864 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9838 | HIS9838 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4964 | 2080_00004‐3
D | 01‐VHIS865 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9838 | HIS9838 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4965 | 2080_00004‐3
D | 01‐VHIS866 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9836 | HIS9836 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4966 | 2080_00004‐3
D | 01‐VHIS867 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9836 | HIS9836 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4967 | 2080_00004‐3
D | 01‐VHIS982 | IP SUPERHEATED STEAM SAMPLE ISOLATION | HIS9609 | HIS9609 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 624 | 622 | 43 | 327.6 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23108 | 23.22 | 4968 | 2080_00004‐3
D | 01‐VHIS983 | IP SUPERHEATED STEAM SAMPLE ISOLATION | HIS9609 | HIS9609 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 624 | 622 | 43 | 327.6 | 2500 | 2500 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23108 | 23.22 | 4969 | 2080_00004‐3
D | 01‐VHIS985 | IP SUPERHEATED STEAM PRESSURE INDICATION ISOLATION | HIS9827 | HIS9827 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4970 | 2080_00004‐3
D | 01‐VHIS986 | IP SUPERHEATED STEAM PRESSURE INDICATION ISOLATION | HIS9827 | HIS9827 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4971 | 2080_00004‐3
D | 01‐VHIS987 | IP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HIS9828 | HIS9828 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4972 | 2080_00004‐3
D | 01‐VHIS988 | IP SUPERHEATED STEAM PRESSURE TRANSMITTER ISOLATION | HIS9828 | HIS9828 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4973 | 2080_00004‐3
D | 01‐VHIS994 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9834 | HIS9834 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4974 | 2080_00004‐3
D | 01‐VHIS995 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9834 | HIS9834 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4975 | 2080_00004‐3
D | 01‐VHIS996 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9836 | HIS9836 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4976 | 2080_00004‐3
D | 01‐VHIS997 | IP SUPERHEATED STEAM FLOW INDICATION ISOLATION | HIS9836 | HIS9836 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 800 | 800 | SW | SW |  | 935 | 65 | 4 | ‐ | HP Valve | 2080_23123 | 23.22 | 4977 | 2080_00004‐3
D | 01‐VHRS803 | COLD REHEAT RETURN PRESSURE TRANSMITTER ISOLATION | HRS8837 | HRS8837 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 783 | 43 | 417.2 | 800 | 800 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23122 | 23.22 | 4978 | 2080_00004‐4
D | 01‐VHRS804 | COLD REHEAT RETURN PRESSURE TRANSMITTER ISOLATION | HRS8837 | HRS8837 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 783 | 43 | 417.2 | 800 | 800 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23122 | 23.22 | 4979 | 2080_00004‐4
D | 01‐VHRS805 | COLD REHEAT RETURN PRESSURE INDICATOR ISOLATION | HRS8838 | HRS8838 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 783 | 43 | 417.2 | 800 | 800 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23122 | 23.22 | 4980 | 2080_00004‐4
D | 01‐VHRS806 | COLD REHEAT RETURN PRESSURE INDICATOR ISOLATION | HRS8838 | HRS8838 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F11 | 624 | 783 | 43 | 417.2 | 800 | 800 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23122 | 23.22 | 4981 | 2080_00004‐4
D | 01‐VHRS807 | REHEATER INLET VENT | HRS9988 | HRS9988 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F22 | 624 | 752 | 43 | 400.2 | 900 | 900 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23132 | 23.22 | 4982 | 2080_00004‐4
D | 01‐VHRS808 | REHEATER INLET VENT | HRS9988 | HRS9988 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F22 | 624 | 752 | 43 | 400.2 | 900 | 900 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23132 | 23.22 | 4983 | 2080_00004‐4
D | 01‐VHRS809 | REHEATER INLET NITROGEN FILL ISOLATION | HRG9102 | HRS9402 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F22 | 624 | 752 | 43 | 400.2 | 2500 | 2500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23105 | 23.22 | 4984 | 2080_00004‐4
D | 01‐VHRS810 | REHEATER INLET NITROGEN FILL CHECK VALVE | HRS9402 | HRS9402 | Steam | NA | NA | 2" | 2" | Check Valve | SA‐335 P11 | SA‐335 P11 | SA‐182 F22 | 624 | 752 | 43 | 400.2 | 2500 | 2500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23130 | 23.22 | 4985 | 2080_00004‐4
D | 01‐VHRS813 | HOT REHEAT OUTLET PRESSURE TRANSMITTER ISOLATION | HRS9803 | HRS9803 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 LTD | 2500 LTD | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23110 | 23.22 | 4986 | 2080_00004‐4
D | 01‐VHRS814 | HOT REHEAT OUTLET PRESSURE TRANSMITTER ISOLATION | HRS9803 | HRS9803 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 LTD | 2500 LTD | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23110 | 23.22 | 4987 | 2080_00004‐4
D | 01‐VHRS820 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9805 | HRS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS920 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4988 | 2080_00004‐4
D | 01‐VHRS821 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9805 | HRS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS921 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4989 | 2080_00004‐4
D | 01‐VHRS822 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9806 | HRS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS922 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4990 | 2080_00004‐4
D | 01‐VHRS823 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9806 | HRS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS923 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 4991 | 2080_00004‐4
D | 01‐VHRS824 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9807 | HRS9807 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS924 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4992 | 2080_00004‐4
D | 01‐VHRS825 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9807 | HRS9807 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS925 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4993 | 2080_00004‐4
D | 01‐VHRS826 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HRS9808 | HRS9808 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS926 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4994 | 2080_00004‐4
D | 01‐VHRS827 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HRS9808 | HRS9808 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS927 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4995 | 2080_00004‐4
D | 01‐VHRS828 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HRS9809 | HRS9809 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | SPARE_446 on valve drawing 2080_23109 Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4996 | 2080_00004‐4
D | 01‐VHRS829 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HRS9809 | HRS9809 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | SPARE_447 on valve drawing 2080_23109 Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4997 | 2080_00004‐4
D | 01‐VHRS832 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9810 | HRS9810 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS932 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4998 | 2080_00004‐4
D | 01‐VHRS833 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9810 | HRS9810 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS933 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 4999 | 2080_00004‐4
D | 01‐VHRS834 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9811 | HRS9811 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS934 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 5000 | 2080_00004‐4
D | 01‐VHRS835 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9811 | HRS9811 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS935 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 5001 | 2080_00004‐4
D | 01‐VHRS836 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9812 | HRS9812 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS936 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 5002 | 2080_00004‐4
D | 01‐VHRS837 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9812 | HRS9812 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS937 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23123 | 23.22 | 5003 | 2080_00004‐4
D | 01‐VHRS838 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9813 | HRS9813 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS938 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 5004 | 2080_00004‐4
D | 01‐VHRS839 | REHEAT FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9813 | HRS9813 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW | Previously 01‐VHRS939 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 5005 | 2080_00004‐4
D | 01‐VHRS848 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER STRAINER DRAIN | HRS9304 | HRS9304 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS‐948 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 5006 | 2080_00004‐4
D | 01‐VHRS849 | REHEAT INTERSTAGE ATTEMPERATOR STRAINER COOLING WATER DRAIN | HRS9304 | HRS9305 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS‐949 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 5007 | 2080_00004‐4
D | 01‐VHRS860 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DRAIN | HRS9302 | HRS9302 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS‐960 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 5008 | 2080_00004‐4
D | 01‐VHRS861 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER DRAIN | HRS9302 | HRS9303 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 800 | 800 | SW | SW | Previously 01‐VHRS‐961 on P&ID Rev D | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23125 | 23.22 | 5009 | 2080_00004‐4
D | 01‐VHRS862 | REHEAT INTERSTAGE ATTEMPERATOR DRAIN | HRS9306 | HRS9306 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 946 | 43 | 508 | 900 | 900 | SW | SW | Previously 01‐VHRS‐962 on P&ID Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23111 | 23.22 | 5010 | 2080_00004‐4
D | 01‐VHRS863 | REHEAT INTERSTAGE ATTEMPERATOR DRAIN | HRS9306 | HRS9307 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 946 | 43 | 508 | 900 | 900 | SW | SW | Previously 01‐VHRS‐963 on P&ID Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23111 | 23.22 | 5011 | 2080_00004‐4
D | 01‐VHRS901 | HOT REHEAT STEAM SAMPLE ISOLATION | HRS9601 | HRS9601 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 624 | 1096 | 43 | 591.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23108 | 23.22 | 5012 | 2080_00004‐4
D | 01‐VHRS902 | HOT REHEAT STEAM SAMPLE ISOLATION | HRS9601 | HRS9601 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 624 | 1096 | 43 | 591.1 | 2500 | 2500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23108 | 23.22 | 5013 | 2080_00004‐4
D | 01‐VHRS903 | HOT REHEAT OUTLET PRESSURE TRANSMITTER ISOLATION | HRS9801 | HRS9801 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 LTD | 2500 LTD | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23110 | 23.22 | 5014 | 2080_00004‐4
D | 01‐VHRS904 | HOT REHEAT OUTLET PRESSURE TRANSMITTER ISOLATION | HRS9801 | HRS9801 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 LTD | 2500 LTD | SW | SW | SPARE_427 on valve drawing 2080_23110 Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23110 | 23.22 | 5015 | 2080_00004‐4
D | 01‐VHRS911 | HOT REHEAT OUTLET PRESSURE INDICATOR ISOLATION | HRS9802 | HRS9802 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 900 | 900 | SW | SW | Previously 01‐VHRS905 on P&ID Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23112 | 23.22 | 5016 | 2080_00004‐4
D | 01‐VHRS912 | HOT REHEAT OUTLET PRESSURE INDICATOR ISOLATION | HRS9802 | HRS9802 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 900 | 900 | SW | SW | Previously 01‐VHRS906 on P&ID Rev D | 935 | 65 | 5 | ‐ | HP Valve | 2080_23112 | 23.22 | 5017 | 2080_00004‐4
D | 01‐VHRS918 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9804 | HRS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 5018 | 2080_00004‐4
D | 01‐VHRS919 | REHEAT INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HRS9804 | HRS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 2500 | 2500 | SW | SW |  | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23109 | 23.22 | 5019 | 2080_00004‐4
D | 01‐VHRS969 | REHEATER INTERSTAGE ATTEMPERATOR DRAIN POT CLEANOUT DRAIN | HRS9308 | HRS9308 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 624 | 946 | 43 | 508 | 1500 | 1500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23116 | 23.22 | 5020 | 2080_00004‐4
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5021 | 2080_00003‐1
D | 01‐VHRS970 | REHEATER INTERSTAGE ATTEMPERATOR DRAIN POT CLEANOUT DRAIN | HRS9308 | HRS9308 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 624 | 946 | 43 | 508 | 1500 | 1500 | SW | SW |  | 935 | 65 | 5 | ‐ | HP Valve | 2080_23116 | 23.22 | 5022 | 2080_00004‐4
D | 01‐VHHS854 | HP ECONOMIZER INLET PRESSURE INDICATOR ISOLATION | HHS8806 | HHS8806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5023 | 2080_00005‐1
D | 01‐VHHS855 | HP ECONOMIZER INLET PRESSURE INDICATOR ISOLATION | HHS8806 | HHS8806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5024 | 2080_00005‐1
D | 01‐VHHS856 | HP FEEDWATER INLET DRAIN | HHS9901 | HHS9901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 5025 | 2080_00005‐1
D | 01‐VHHS857 | HP FEEDWATER INLET DRAIN | HHS9901 | HHS9902 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 5026 | 2080_00005‐1
D | 01‐VHHS858 | HP FEEDWATER INLET DRAIN | HHS9903 | HHS9903 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 5027 | 2080_00005‐1
D | 01‐VHHS859 | HP FEEDWATER INLET DRAIN | HHS9903 | HHS9904 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 5028 | 2080_00005‐1
D | 01‐VHHS900 | HP ECONOMIZER DRAIN | HHS9909 | HHS9317 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5029 | 2080_00005‐1
D | 01‐VHHS905 | HP ECONOMIZER DRAIN | HHS9932 | HHS9933 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5030 | 2080_00005‐1
D | 01‐VHHS906 | HP ECONOMIZER DRAIN | HHS9917 | HHS9946 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5031 | 2080_00005‐1
D | 01‐VHHS907 | HP DRUM LCV BYPASS | HHS9247 | HHS9248 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 5032 | 2080_00005‐1
D | 01‐VHHS912 | HP FEEDWATER INLET DRAIN | HHS9905 | HHS9905 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 5033 | 2080_00005‐1
D | 01‐VHHS913 | HP FEEDWATER INLET DRAIN | HHS9905 | HHS9906 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23113 | 23.22 | 5034 | 2080_00005‐1
D | 01‐VHHS914 | HP ECONOMIZER INLET PRESSURE TRANSMITTER ISOLATION | HHS9806 | HHS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5035 | 2080_00005‐1
D | 01‐VHHS915 | HP ECONOMIZER INLET PRESSURE TRANSMITTER ISOLATION | HHS9806 | HHS9806 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5036 | 2080_00005‐1
D | 01‐VHHS916 | HP FEEDWATER INLET PRESSURE TRANSMITTER ISOLATION | HHS9801 | HHS9801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5037 | 2080_00005‐1
D | 01‐VHHS917 | HP FEEDWATER INLET PRESSURE TRANSMITTER ISOLATION | HHS9801 | HHS9801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5038 | 2080_00005‐1
D | 01‐VHHS918 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9802 | HHS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5039 | 2080_00005‐1
D | 01‐VHHS919 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9802 | HHS9802 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5040 | 2080_00005‐1
D | 01‐VHHS920 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9803 | HHS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5041 | 2080_00005‐1
D | 01‐VHHS921 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9803 | HHS9803 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5042 | 2080_00005‐1
D | 01‐VHHS922 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9804 | HHS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5043 | 2080_00005‐1
D | 01‐VHHS923 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9804 | HHS9804 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5044 | 2080_00005‐1
D | 01‐VHHS924 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9805 | HHS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5045 | 2080_00005‐1
D | 01‐VHHS925 | HP FEEDWATER INLET FLOW TRANSMITTER ISOLATION | HHS9805 | HHS9805 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5046 | 2080_00005‐1
D | 01‐VHHS926 | HP BOILER FILL ISOLATION | HHS9121 | HHS9122 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5047 | 2080_00005‐1
D | 01‐VHHS927 | HP BOILER FILL CHECK VALVE | HHS9122 | HHS9122 | Water | NA | NA | 2" | 2" | Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23118 | 23.22 | 5048 | 2080_00005‐1
D | 01‐VHHS928 | HP BOILER FILL ISOLATION | HHS9122 | HHS9123 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5049 | 2080_00005‐1
D | 01‐VHHS929 | HP ECONOMIZER DRAIN | HHS9313 | HHS9314 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5050 | 2080_00005‐1
D | 01‐VHHS930 | HP ECONOMIZER DRAIN | HHS9910 | HHS9912 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5051 | 2080_00005‐1
D | 01‐VHHS931 | HP ECONOMIZER DRAIN | HHS9913 | HHS9915 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5052 | 2080_00005‐1
D | 01‐VHHS932 | HP ECONOMIZER DRAIN | HHS9916 | HHS9917 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5053 | 2080_00005‐1
D | 01‐VHHS933 | HP ECONOMIZER DRAIN | HHS9918 | HHS9920 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5054 | 2080_00005‐1
D | 01‐VHHS934 | HP ECONOMIZER DRAIN | HHS9921 | HHS9923 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5055 | 2080_00005‐1
D | 01‐VHHS935 | HP ECONOMIZER DRAIN | HHS9924 | HHS9926 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5056 | 2080_00005‐1
D | 01‐VHHS936 | HP ECONOMIZER DRAIN | HHS9927 | HHS9929 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5057 | 2080_00005‐1
D | 01‐VHHS937 | HP ECONOMIZER DRAIN | HHS9930 | HHS9932 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5058 | 2080_00005‐1
D | 01‐VHHS938 | HP ECONOMIZER DRAIN | HHS9926 | HHS9312 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5059 | 2080_00005‐1
D | 01‐VHHS939 | HP ECONOMIZER VENT | HHS9951 | HHS9953 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5060 | 2080_00005‐1
D | 01‐VHHS940 | HP ECONOMIZER VENT | HHS9954 | HHS9956 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5061 | 2080_00005‐1
D | 01‐VHHS941 | HP ECONOMIZER VENT | HHS9957 | HHS9959 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5062 | 2080_00005‐1
D | 01‐VHHS942 | HP ECONOMIZER VENT | HHS9960 | HHS9962 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5063 | 2080_00005‐1
D | 01‐VHHS943 | HP ECONOMIZER VENT | HHS9963 | HHS9965 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5064 | 2080_00005‐1
D | 01‐VHHS944 | HP ECONOMIZER VENT | HHS9966 | HHS9968 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5065 | 2080_00005‐1
D | 01‐VHHS945 | HP ECONOMIZER VENT | HHS9969 | HHS9971 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5066 | 2080_00005‐1
D | 01‐VHHS946 | HP ECONOMIZER VENT | HHS9972 | HHS9974 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 692 | 199 | 366.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5067 | 2080_00005‐1
D | 01‐VHHS947 | HP ECONOMIZER VENT | HHS9975 | HHS9977 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5068 | 2080_00005‐1
D | 01‐VHHS961 | HP ECONOMIZER DRAIN | HHS9908 | HHS9909 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 374 | 199 | 189.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5069 | 2080_00005‐1
D | 01‐VHHS801 | HP SATURATED STEAM VENT | HHS8978 | HHS8978 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5070 | 2080_00005‐2
D | 01‐VHHS802 | HP SATURATED STEAM VENT | HHS8978 | HHS8978 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5071 | 2080_00005‐2
D | 01‐VHHS950 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS9807 | HHS9807 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5072 | 2080_00005‐2
D | 01‐VHHS951 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS9807 | HHS9807 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5073 | 2080_00005‐2
D | 01‐VHHS952 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS9808 | HHS9808 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5074 | 2080_00005‐2
D | 01‐VHHS953 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS9808 | HHS9808 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5075 | 2080_00005‐2
D | 01‐VHHS954 | HP DRUM PRESSURE INDICATOR ISOLATION | HHS8802 | HHS8802 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5076 | 2080_00005‐2
D | 01‐VHHS955 | HP DRUM PRESSURE INDICATOR ISOLATION | HHS8802 | HHS8802 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5077 | 2080_00005‐2
D | 01‐VHHS956 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS8801 | HHS8801 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5078 | 2080_00005‐2
D | 01‐VHHS957 | HP DRUM PRESSURE TRANSMITTER ISOLATION | HHS8801 | HHS8801 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5079 | 2080_00005‐2
D | 01‐VHHS958 | HP DRUM NITROGEN SUPPLY NRV | HRG9103 | HHS8401 | Water/Steam | NA | NA | 2" | 2" | Stop Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23101 | 23.22 | 5080 | 2080_00005‐2
D | 01‐VHHS959 | HP DRUM NITROGEN SUPPLY ISOLATION | HHS8401 | HHS8401 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5081 | 2080_00005‐2
D | 01‐VHHS963 | HP DRUM LEVEL GAUGE ISOLATION | HHS9814 | HHS9814 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5082 | 2080_00005‐2
D | 01‐VHHS964 | HP DRUM LEVEL GAUGE ISOLATION | HHS9814 | HHS9815 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5083 | 2080_00005‐2
D | 01‐VHHS965 | HP DRUM LEVEL GAUGE DRAIN | HHS9934 | HHS9935 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5084 | 2080_00005‐2
D | 01‐VHHS966 | HP DRUM LEVEL GAUGE DRAIN | HHS9934 | HHS9934 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5085 | 2080_00005‐2
D | 01‐VHHS967 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9811 | HHS9811 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5086 | 2080_00005‐2
D | 01‐VHHS968 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9811 | HHS9811 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5087 | 2080_00005‐2
D | 01‐VHHS969 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9813 | HHS9813 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5088 | 2080_00005‐2
D | 01‐VHHS970 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9813 | HHS9813 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5089 | 2080_00005‐2
D | 01‐VHHS971 | HP DRUM LEVEL GAUGE ISOLATION | HHS9824 | HHS9824 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5090 | 2080_00005‐2
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5091 | 2080_00003‐1
D | 01‐VHHS972 | HP DRUM LEVEL GAUGE DRAIN | HHS9937 | HHS9937 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5092 | 2080_00005‐2
D | 01‐VHHS973 | HP DRUM LEVEL GAUGE DRAIN | HHS9936 | HHS9938 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5093 | 2080_00005‐2
D | 01‐VHHS974 | HP DRUM LEVEL GAUGE DRAIN | HHS9936 | HHS9936 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5094 | 2080_00005‐2
D | 01‐VHHS975 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9821 | HHS9821 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5095 | 2080_00005‐2
D | 01‐VHHS976 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9821 | HHS9821 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5096 | 2080_00005‐2
D | 01‐VHHS977 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9823 | HHS9823 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5097 | 2080_00005‐2
D | 01‐VHHS978 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9823 | HHS9823 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5098 | 2080_00005‐2
D | 01‐VHHS979 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9818 | HHS9818 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5099 | 2080_00005‐2
D | 01‐VHHS980 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9818 | HHS9818 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5100 | 2080_00005‐2
D | 01‐VHHS981 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9820 | HHS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5101 | 2080_00005‐2
D | 01‐VHHS982 | HP DRUM LEVEL TRANSMITTER ISOLATION | HHS9820 | HHS9820 | Water/Steam | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5102 | 2080_00005‐2
D | 01‐VHHS983 | HP DRUM LEVEL GAUGE ISOLATION | HHS9824 | HHS9825 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5103 | 2080_00005‐2
D | 01‐VHHS984 | HP DRUM LEVEL GAUGE ISOLATION | HHS9826 | HHS9827 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5104 | 2080_00005‐2
D | 01‐VHHS985 | HP DRUM LEVEL GAUGE ISOLATION | HHS9826 | HHS9826 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5105 | 2080_00005‐2
D | 01‐VHHS986 | HP DRUM LEVEL GAUGE ISOLATION | HHS9816 | HHS9816 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5106 | 2080_00005‐2
D | 01‐VHHS987 | HP DRUM LEVEL GAUGE ISOLATION | HHS9816 | HHS9817 | Water/Steam | NA | NA | 2" | 2" | y globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5107 | 2080_00005‐2
D | 01‐VHHS988 | HP DRUM INLET CHEMICAL INJECTION ISOLATION | HHS9502 | HHS9502 | Water | NA | NA | 1" | 1" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23107 | 23.22 | 5108 | 2080_00005‐2
D | 01‐VHHS989 | HP DRUM INLET CHEMICAL INJECTION CHECK VALVE | HHS9502 | HHS9502 | Water | NA | NA | 1" | 1" | Check Valve | SA‐106 C | SA‐106 C | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23119 | 23.22 | 5109 | 2080_00005‐2
D | 01‐VHHS991 | HP DRUM WATER SAMPLE ISOLATION | HHS9603 | HHS9603 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5110 | 2080_00005‐2
D | 01‐VHHS992 | HP DRUM WATER SAMPLE ISOLATION | HHS9603 | HHS9603 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5111 | 2080_00005‐2
D | 01‐VHHS994 | HP SPARGING STEAM DRAIN | HHS9939 | HHS9939 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5112 | 2080_00005‐2
D | 01‐VHHS995 | HP SPARGING STEAM DRAIN | HHS9939 | HHS9940 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5113 | 2080_00005‐2
D | 01‐VHHS996 | HP SPARGING STEAM STRAINER DRAIN | HHS9941 | HHS9941 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5114 | 2080_00005‐2
D | 01‐VHHS997 | HP SPARGING STEAM STRAINER DRAIN | HHS9941 | HHS9942 | Water/Steam | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5115 | 2080_00005‐2
D | 01‐VHHS998 | HP SATURATED STEAM SAMPLE ISOLATION | HHS9605 | HHS9605 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23108 | 23.22 | 5116 | 2080_00005‐2
D | 01‐VHHS999 | HP SATURATED STEAM SAMPLE ISOLATION | HHS9605 | HHS9605 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23108 | 23.22 | 5117 | 2080_00005‐2
D | 01‐VHHS803 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8828 | HHS8828 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5118 | 2080_00005‐3
D | 01‐VHHS804 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8828 | HHS8828 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5119 | 2080_00005‐3
D | 01‐VHHS805 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8829 | HHS8829 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5120 | 2080_00005‐3
D | 01‐VHHS806 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8829 | HHS8829 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5121 | 2080_00005‐3
D | 01‐VHHS807 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8830 | HHS8830 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5122 | 2080_00005‐3
D | 01‐VHHS808 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8830 | HHS8830 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5123 | 2080_00005‐3
D | 01‐VHHS809 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8831 | HHS8831 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5124 | 2080_00005‐3
D | 01‐VHHS810 | HP SUPERHEATER 1 INLET DRAIN POT LEVEL SWITCH ISOLATION | HHS8831 | HHS8831 | Water/Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23109 | 23.22 | 5125 | 2080_00005‐3
D | 01‐VHHS811 | HP SUPERHEATER 1 TO 2 CROSSOVER VENT | HHS8984 | HHS8984 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 2741 | 884 | 189 | 473.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23105 | 23.22 | 5126 | 2080_00005‐3
D | 01‐VHHS812 | HP SUPERHEATER 1 TO 2 CROSSOVER VENT | HHS8984 | HHS8984 | Steam | NA | NA | 2" | 2" | Globe Valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 2741 | 884 | 189 | 473.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23105 | 23.22 | 5127 | 2080_00005‐3
D | 01‐VHHS813 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8832 | HHS8832 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5128 | 2080_00005‐3
D | 01‐VHHS814 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8832 | HHS8832 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5129 | 2080_00005‐3
D | 01‐VHHS815 | HP SUPERHEATER OUTLET PRESSURE INDICATOR ISOLATION | HHS8833 | HHS8833 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5130 | 2080_00005‐3
D | 01‐VHHS816 | HP SUPERHEATER OUTLET PRESSURE INDICATOR ISOLATION | HHS8833 | HHS8833 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5131 | 2080_00005‐3
D | 01‐VHHS818 | HP SUPERHEATER OUTLET DRAIN | HHS8313 | HHS8313 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23104 | 23.22 | 5132 | 2080_00005‐3
D | 01‐VHHS819 | HP SUPERHEATER OUTLET DRAIN | HHS8313 | HHS8314 | Water/Steam | NA | NA | 2" | 2" | Y globe valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23104 | 23.22 | 5133 | 2080_00005‐3
D | 01‐VHHS820 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8835 | HHS8835 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5134 | 2080_00005‐3
D | 01‐VHHS821 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8835 | HHS8835 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5135 | 2080_00005‐3
D | 01‐VHHS822 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8837 | HHS8837 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5136 | 2080_00005‐3
D | 01‐VHHS823 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8837 | HHS8837 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5137 | 2080_00005‐3
D | 01‐VHHS824 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8839 | HHS8839 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5138 | 2080_00005‐3
D | 01‐VHHS825 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8839 | HHS8839 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5139 | 2080_00005‐3
D | 01‐VHHS826 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8841 | HHS8841 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5140 | 2080_00005‐3
D | 01‐VHHS827 | HP SUPERHEATER OUTLET FLOW TRANSMITTER ISOLATION | HHS8841 | HHS8841 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5141 | 2080_00005‐3
D | 01‐VHHS828 | HP SUPERHEATED STEAM SAMPLE ISOLATION | HHS8607 | HHS8607 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 2534 | 1098 | 174.7 | 592 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23108 | 23.22 | 5142 | 2080_00005‐3
D | 01‐VHHS829 | HP SUPERHEATED STEAM SAMPLE ISOLATION | HHS8607 | HHS8607 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐312 TP316H | SA‐312 TP316H | SA‐182 F316 (L) | 2534 | 1098 | 174.7 | 592 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23108 | 23.22 | 5143 | 2080_00005‐3
D | 01‐VHHS830 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8842 | HHS8842 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5144 | 2080_00005‐3
D | 01‐VHHS831 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8842 | HHS8842 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5145 | 2080_00005‐3
D | 01‐VHHS832 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8843 | HHS8843 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5146 | 2080_00005‐3
D | 01‐VHHS833 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8843 | HHS8843 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5147 | 2080_00005‐3
D | 01‐VHHS834 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8844 | HHS8844 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5148 | 2080_00005‐3
D | 01‐VHHS835 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8844 | HHS8844 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5149 | 2080_00005‐3
D | 01‐VHHS836 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8845 | HHS8845 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5150 | 2080_00005‐3
D | 01‐VHHS837 | HP INTERSTAGE ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8845 | HHS8845 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5151 | 2080_00005‐3
D | 01‐VHHS838 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HHS8846 | HHS8846 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5152 | 2080_00005‐3
D | 01‐VHHS839 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HHS8846 | HHS8846 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5153 | 2080_00005‐3
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5154 | 2080_00003‐1
D | 01‐VHHS840 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HHS8847 | HHS8847 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5155 | 2080_00005‐3
D | 01‐VHHS841 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DIFFERENTIAL PRESSURE TRANSMITTER ISOLATION | HHS8847 | HHS8847 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5156 | 2080_00005‐3
D | 01‐VHHS842 | HP INTERSTAGE ATTEMPERATOR COOLING WATER STRAINER DRAIN | HHS8318 | HHS8318 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 5157 | 2080_00005‐3
D | 01‐VHHS843 | HP INTERSTAGE ATTEMPERATOR COOLING WATER STRAINER DRAIN | HHS8318 | HHS8316 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 5158 | 2080_00005‐3
D | 01‐VHHS846 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8848 | HHS8848 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5159 | 2080_00005‐3
D | 01‐VHHS847 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8848 | HHS8848 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5160 | 2080_00005‐3
D | 01‐VHHS848 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8849 | HHS8849 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5161 | 2080_00005‐3
D | 01‐VHHS849 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8849 | HHS8849 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5162 | 2080_00005‐3
D | 01‐VHHS850 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8850 | HHS8850 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5163 | 2080_00005‐3
D | 01‐VHHS851 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8850 | HHS8850 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5164 | 2080_00005‐3
D | 01‐VHHS852 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8851 | HHS8851 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5165 | 2080_00005‐3
D | 01‐VHHS853 | HP FINAL ATTEMPERATOR COOLING WATER FLOW TRANSMITTER ISOLATION | HHS8851 | HHS8851 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23109 | 23.22 | 5166 | 2080_00005‐3
D | 01‐VHHS863 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DRAIN | HHS8319 | HHS8319 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 5167 | 2080_00005‐3
D | 01‐VHHS864 | HP INTERSTAGE ATTEMPERATOR COOLING WATER DRAIN | HHS8319 | HHS8322 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW |  | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23106 | 23.22 | 5168 | 2080_00005‐3
D | 01‐VHHS865 | HP INTERSTAGE ATTEMPERATOR COOLING WATER VENT | HHS8321 | HHS8321 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 1032 | 189 | 555.6 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS971 on valve drawing 2080_23113 Rev D | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23113 | 23.22 | 5169 | 2080_00005‐3
D | 01‐VHHS866 | HP INTERSTAGE ATTEMPERATOR COOLING WATER VENT | HHS8321 | HHS8320 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 1032 | 189 | 555.6 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23106 | 23.22 | 5170 | 2080_00005‐3
D | 01‐VHHS867 | HP SUPERHEATER 1 INLET DRAIN POT CLEANOUT DRAIN | HHS8323 | HHS8323 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23114 | 23.22 | 5171 | 2080_00005‐3
D | 01‐VHHS868 | HP SUPERHEATER 1 INLET DRAIN POT CLEANOUT DRAIN | HHS8323 | HHS8323 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23114 | 23.22 | 5172 | 2080_00005‐3
D | 01‐VHHS871 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8853 | HHS8853 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW | SPARE_423 on valve drawing 2080_23110 Rev D | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5173 | 2080_00005‐3
D | 01‐VHHS872 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8852 | HHS8852 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5174 | 2080_00005‐3
D | 01‐VHHS873 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8853 | HHS8853 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5175 | 2080_00005‐3
D | 01‐VHHS874 | HP SUPERHEATER OUTLET PRESSURE TRANSMITTER ISOLATION | HHS8852 | HHS8852 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW | SPARE_424 on valve drawing 2080_23110 Rev D | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23110 | 23.22 | 5176 | 2080_00005‐3
D | 01‐VHHS909 | HP INTERSTAGE ATTEMPERATOR DRAIN POT CLEANOUT DRAIN | HHS9315 | HHS9315 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2741 | 1032 | 189 | 555.6 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23115 | 23.22 | 5177 | 2080_00005‐3
D | 01‐VHHS910 | HP INTERSTAGE ATTEMPERATOR DRAIN POT CLEANOUT DRAIN | HHS9315 | HHS9315 | Water/Steam | NA | NA | 1" | 1" | Gate Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2741 | 1032 | 189 | 555.6 | 2500 LTD | 2500 LTD | SW | SW |  | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23115 | 23.22 | 5178 | 2080_00005‐3
D | 01‐VHLS801 | PREHEATER DRAIN | HLS8901 | HLS8901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5179 | 2080_00006‐1
D | 01‐VHLS802 | PREHEATER DRAIN | HLS8901 | HLS8902 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 9 & 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5180 | 2080_00006‐1
D | 01‐VHLS803 | LP FEEDWATER INLET PRESSURE TRANSMITTER ISOLATION | HLS8801 | HLS8801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 5181 | 2080_00006‐1
D | 01‐VHLS804 | LP FEEDWATER INLET PRESSURE TRANSMITTER ISOLATION | HLS8801 | HLS8801 | Water | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23123 | 23.22 | 5182 | 2080_00006‐1
D | 01‐VHLS807 | PREHEATER DRAIN | HLS8905 | HLS8905 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5183 | 2080_00006‐1
D | 01‐VHLS810 | PREHEATER DRAIN | HLS8905 | HLS8906 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5184 | 2080_00006‐1
D | 01‐VHLS823 | PREHEATER DRAIN | HLS9907 | HLS8904 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 9 & 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5185 | 2080_00006‐1
D | 01‐VHLS824 | PREHEATER DRAIN | HLS9947 | HLS8903 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 9 & 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5186 | 2080_00006‐1
D | 01‐VHLS829 | PREHEATER DRAIN | HLS8907 | HLS8907 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW | SPARE_27 on valve drawing 2080_23125 Rev D | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5187 | 2080_00006‐1
D | 01‐VHLS830 | PREHEATER DRAIN | HLS8907 | HLS8908 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW | SPARE_28 on valve drawing 2080_23125 Rev D | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5188 | 2080_00006‐1
D | 01‐VHLS851 | PREHEATER INLET VENT | HLS8951 | HLS8951 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW | SPARE_134 on valve drawing 2080_23120 Rev D | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5189 | 2080_00006‐1
D | 01‐VHLS852 | PREHEATER INLET VENT | HLS8951 | HLS8952 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 356 | 41.4 | 180 | 800 | 800 | SW | SW | SPARE_398 on valve drawing 2080_23120 Rev D | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5190 | 2080_00006‐1
D | 01‐VHLS902 | PREHEATER DRAIN | HLS9901 | HLS9901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5191 | 2080_00006‐1
D | 01‐VHLS903 | PREHEATER DRAIN | HLS9901 | HLS9902 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 345 | 41.4 | 174 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5192 | 2080_00006‐1
D | 01‐VHLS906 | PREHEATER VENT | HLS9955 | HLS9956 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW | Tag previously 01‐VHLS909 (redundant with LB valve) | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5193 | 2080_00006‐1
D | 01‐VHLS910 | PREHEATER VENT | HLS9958 | HLS9959 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5194 | 2080_00006‐1
D | 01‐VHLS911 | PREHEATER DRAIN | HLS9903 | HLS9905 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5195 | 2080_00006‐1
D | 01‐VHLS912 | PREHEATER DRAIN | HLS9906 | HLS9907 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5196 | 2080_00006‐1
D | 01‐VHLS913 | PREHEATER DRAIN | HLS9942 | HLS9944 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5197 | 2080_00006‐1
D | 01‐VHLS914 | PREHEATER VENT | HLS9961 | HLS9962 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5198 | 2080_00006‐1
D | 01‐VHLS915 | PREHEATER VENT | HLS9964 | HLS9965 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5199 | 2080_00006‐1
D | 01‐VHLS916 | PREHEATER DRAIN | HLS9945 | HLS9947 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5200 | 2080_00006‐1
D | 01‐VHLS917 | PREHEATER VENT | HLS9967 | HLS9968 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5201 | 2080_00006‐1
D | 01‐VHLS918 | PREHEATER DRAIN | HLS9948 | HLS9949 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5202 | 2080_00006‐1
D | 01‐VHLS919 | PREHEATER VENT | HLS9970 | HLS9971 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5203 | 2080_00006‐1
D | 01‐VHLS920 | PREHEATER DRAIN | HLS9910 | HLS9912 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5204 | 2080_00006‐1
D | 01‐VHLS921 | PREHEATER DRAIN | HLS9912 | HLS9913 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 9 & 1 | ‐ | HP Valve | 2080_23125 | 23.22 | 5205 | 2080_00006‐1
D | 01‐VHLS922 | PREHEATER VENT | HLS9972 | HLS9973 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5206 | 2080_00006‐1
D | 01‐VHLS984 | PREHEATER VENT | HLS9952 | HLS9953 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 490 | 41.4 | 254.7 | 800 | 800 | SW | SW |  | 901 | 62 | 1 | ‐ | HP Valve | 2080_23120 | 23.22 | 5207 | 2080_00006‐1
D | 01‐VHBD801 | BLOWDOWN TANK PRESSURE INDICATOR ISOLATION | HBD9801 | HBD9801 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23123 | 23.22 | 5208 | 2080_00007‐1
D | 01‐VHBD802 | BLOWDOWN TANK PRESSURE TRANSMITTER ISOLATION | HBD9802 | HBD9802 | Steam | NA | NA | 3/4" | 3/4" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23123 | 23.22 | 5209 | 2080_00007‐1
D | 01‐VHBD803 | BLOWDOWN TANK LEVEL GAUGE ISOLATION | HBD9803 | HBD9803 | Water/Steam | NA | NA | 3/4" | 3/4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23127 | 23.22 | 5210 | 2080_00007‐1
D | 01‐VHBD804 | BLOWDOWN TANK LEVEL GAUGE ISOLATION | HBD9804 | HBD9804 | Water/Steam | NA | NA | 3/4" | 3/4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23127 | 23.22 | 5211 | 2080_00007‐1
D | 01‐VHBD805 | BLOWDOWN TANK LEVEL TRANSMITTER ISOLATION | HBD9805 | HBD9805 | Water/Steam | NA | NA | 3/4" | 3/4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23127 | 23.22 | 5212 | 2080_00007‐1
D | 01‐VHBD806 | BLOWDOWN TANK LEVEL TRANSMITTER ISOLATION | HBD9806 | HBD9806 | Water/Steam | NA | NA | 3/4" | 3/4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23127 | 23.22 | 5213 | 2080_00007‐1
D | 01‐VHBD901 | BLOWDOWN TANK LOW POINT DRAIN | HBD9901 | HBD9901 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 800 | 800 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23125 | 23.22 | 5214 | 2080_00007‐1
D | 01‐VHBD902 | BLOWDOWN TANK LEVEL GAUGE DRAIN | HBD9920 | HBD9920 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW | 01‐VHLS996 on valve drawing 2080_23106 Rev D | 78 | 5 | 9 | ‐ | HP Valve | 2080_23106 | 23.22 | 5215 | 2080_00007‐1
D | 01‐VHBD903 | BLOWDOWN TANK LEVEL GAUGE DRAIN | HBD9920 | HBD9920 | Water | NA | NA | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS983 on valve drawing 2080_23106 Rev D | 78 | 5 | 9 | ‐ | HP Valve | 2080_23106 | 23.22 | 5216 | 2080_00007‐1
D | 01‐VHBD907 | BLOWDOWN QUENCH WATER DRAIN | HBD9914 | HBD9914 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23113 | 23.22 | 5217 | 2080_00007‐1
D | 01‐VHBD908 | BLOWDOWN QUENCH WATER DRAIN | HBD9914 | HBD9914 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW |  | 78 | 5 | 9 | ‐ | HP Valve | 2080_23113 | 23.22 | 5218 | 2080_00007‐1
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5219 | 2080_00003‐1
D | 01‐VHBD909 | BLOWDOWN QUENCH WATER BYPASS | HBD9111 | HBD9112 | Water/Steam | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 58 | 750 | 4 | 399 | 2500 | 2500 | SW | SW | SPARE 01‐VHHS984 on valve drawing 2080_23106 Rev D | 78 | 5 | 9 | ‐ | HP Valve | 2080_23106 | 23.22 | 5220 | 2080_00007‐1
E | 01‐VHHS861 | HP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HHS8931 | HHS8931 | Water | NA | NA | 2" | 2" | Y globe valve | SA‐106 C | SA‐106 C | SA‐105 | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | SW | SW | TBD on valve drawing 2080_23103 Rev C | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5221 | 2080_00007‐1
E | 01‐VHHS862 | HP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HHS8931 | HHS8931 | Water | NA | NA | 2" | 2" | Y globe valve | SA‐106 C | SA‐106 C | SA‐105 | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | SW | SW | TBD on valve drawing 2080_23103 Rev C | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5222 | 2080_00007‐1
D | 01‐VHHS960 | HP EVAPORATOR DRAIN | HHS9994 | HBD9906 | Water | NA | NA | 2" | 2" | Y globe valve | SA‐106 C | SA‐106 C | SA‐105N | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | SW | SW |  | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23103 | 23.22 | 5223 | 2080_00007‐1
D | 01‐VHIS908 | IP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HIS9934 | HIS9934 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105 | 812 | 522 | 56 | 272.2 | 800 | 800 | SW | SW | SPARE 01‐VHLS949 on valve drawing 2080_23125 Rev D | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 5224 | 2080_00007‐1
D | 01‐VHIS909 | IP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HIS9934 | HIS9934 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105 | 812 | 522 | 56 | 272.2 | 800 | 800 | SW | SW | SPARE 01‐VHLS939 on valve drawing 2080_23125 Rev D | 935 | 65 | 4 | ‐ | HP Valve | 2080_23125 | 23.22 | 5225 | 2080_00007‐1
D | 01‐VHLS928 | LP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HLS9932 | HLS9932 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105 | 196 | 386 | 13.5 | 196.5 | 800 | 800 | SW | SW | SPARE 01‐VHLS964 on valve drawing 2080_23125 Rev D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 5226 | 2080_00007‐1
D | 01‐VHLS929 | LP INTERMITTENT BLOWDOWN LOW POINT DRAIN | HLS9932 | HLS9932 | Water | NA | NA | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105 | 196 | 386 | 13.5 | 196.5 | 800 | 800 | SW | SW | SPARE 01‐VHLS965 on valve drawing 2080_23125 Rev D | 196 | 14 | 2 | ‐ | HP Valve | 2080_23125 | 23.22 | 5227 | 2080_00007‐1
D | 01‐MOV‐HLS904 | LP STEAM SPARGING | HLS9125 | HLS9152 | Steam | MOVDIG | FIP | 3" | 3" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 425 | 454 | 29.3 | 234.4 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 638 | 44 | 8 | ‐ | HP Valve | 2080_23326 | 23.3 | 5228 | 2080_00003‐1
D | 01‐MOV‐HLS905 | LP STEAM STARTUP VENT STOP | HLS9988 | HLS9993 | Steam | MOVDIG | FIP | 2" | 2" | Globe Valve | SA‐106 B | SA‐106 B | SA‐105N | 247 | 623 | 17 | 328.5 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 196 | 14 | 2 | ‐ | HP Valve | 2080_23329 | 23.3 | 5229 | 2080_00003‐2
D | 01‐MOV‐HLS906 | LP STEAM OUTLET STOP | HLS9165 | HLS9166 | Steam | MOVDIG | FIP | 14" | 14" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 131 | 623 | 9 | 328.5 | 150 | 150 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 196 | 14 | 2 | ‐ | HP Valve | 2080_23303 | 23.3 | 5230 | 2080_00003‐2
D | 01‐MOV‐HIS901 | IP FEEDWATER INLET STOP VALVE | HIS9101 | HIS9102 | Water | MOVDIG | FIP | 6" | 6" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 2100 | 145 | 3 | Bypass Equalizer Type 4 | HP Valve | 2080_23328 | 23.3 | 5231 | 2080_00004‐1
D | 01‐MOV‐HIS903 | IP ECONOMIZER VENT STOP | HIS9978 | HIS9956 | Water | MOVDIG | FIP | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 2100 | 145 | 4 & 3 | ‐ | HP Valve | 2080_23306 | 23.3 | 5232 | 2080_00004‐1
D | 01‐MOV‐HIS904 | IP FEEDWATER FGH STOP VALVE | HIS9914 | HIS9196 | Water | MOVDIG | FIP | 4" | 4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 589 | 96.5 | 309.2 | 1500 | 1500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 2100 | 145 | 3 & 4 | Bypass Equalizer Type 4 | HP Valve | 2080_23319 | 23.3 | 5233 | 2080_00004‐1
D | 01‐MOV‐HIS909 | IP SPARGING STEAM STOP | HIS9140 | HIS9140 | Steam | MOVDIG | FIP | 3" | 3" | Globe Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 656 | 498 | 45.2 | 259 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 638 | 44 | 8 | ‐ | HP Valve | 2080_23305 | 23.3 | 5234 | 2080_00004‐2
D | 01‐MOV‐HIS910 | IP TO DA PEGGING | HIS9202 | HIS9202 | Steam | MOVDIG | FIP | 3" | 3" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 502 | 43 | 261.1 | 1500 | 1500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | HP Valve | 2080_23325 | 23.3 | 5235 | 2080_00004‐2
D | 01‐MOV‐HIS906 | IP SUPERHEATER OUTLET VENT | HIS9966 | HIS9967 | Steam | MOVDIG | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | HP Valve | 2080_23310 | 23.3 | 5236 | 2080_00004‐3
D | 01‐MOV‐HIS908 | IP STEAM STOP | HIS9147 | HIS9190 | Steam | MOVDIG | FIP | 8" | 8" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 624 | 622 | 43 | 327.6 | 300 SPL | 300 SPL | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | Bypass Equalizer Type 4 | HP Valve | 2080_23304 | 23.3 | 5237 | 2080_00004‐3
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5238 | 2080_00003‐1
D | 01‐MOV‐HRS904 | REHEAT OUTLET STARTUP VENT STOP | HRS9973 | HRS9976 | Steam | MOVDIG | FIP | 4" | 4" | Globe Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 2500 | 2500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 5 | ‐ | HP Valve | 2080_23332 | 23.3 | 5239 | 2080_00004‐4
D | 01‐MOV‐HRS912 | RHT ATTEMPERATOR SPRAY WATER STOP | HRS9178 | HRS9179 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 1400 | 374 | 96.5 | 189.9 | 1500 | 1500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 2100 | 145 | 3 | ‐ | HP Valve | 2080_23316 | 23.3 | 5240 | 2080_00004‐4
D | 01‐MOV‐HHS901 | HP FEEDWATER STOP | HHS9105 | HHS9199 | Water | MOVDIG | FIP | 12" | 12" | Gate Valve | SA‐106 C | SA‐106 C | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2000 | 2000 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 6150 | 424 | 7 & 6 | Bypass Equalizer Type 4 | HP Valve | 2080_23321 | 23.3 | 5241 | 2080_00005‐1
D | 01‐MOV‐HHS902 | HP ECONOMIZER VENT | HHS9977 | HHS9978 | Water | MOVDIG | FIP | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2886 | 690 | 199 | 365.7 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23307 | 23.3 | 5242 | 2080_00005‐1
D | 01‐MOV‐HHS904 | HP SPARGING STEAM | HHS9161 | HHS9218 | Steam | MOVDIG | FIP | 4" | 4" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 2773 | 684 | 191.2 | 362.4 | 1500 SPL | 1500 SPL | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 & 8 | Bypass Equalizer Type 4 | HP Valve | 2080_23331 | 23.3 | 5243 | 2080_00005‐2
D | 01‐MOV‐HHS906 | HP STEAM OUTLET STOP | HHS9220 | HHS9189 | Steam | MOVDIG | FIP | 16" | 16" | Parallel Slide Gate | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2150 SPL | 2150 SPL | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | Bypass Equalizer Type 4 | HP Valve | 2080_23322 | 23.3 | 5244 | 2080_00005‐3
D | 01‐MOV‐HHS907 | HP STEAM OUTLET STOP VALVE BYPASS | HHS9192 | HHS9192 | Steam | MOVDIG | FIP | 12" | 12" | Gate Valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 SPL | 2500 SPL | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | Bypass Equalizer Type 4 | HP Valve | 2080_23324 | 23.3 | 5245 | 2080_00005‐3
D | 01‐MOV‐HHS908 | HP ATTEMPERATOR SPRAY WATER STOP | HHS9195 | HHS9196 | Water | MOVDIG | FIP | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23317 | 23.3 | 5246 | 2080_00005‐3
D | 01‐MOV‐HHS913 | HP SUPERHEATER OUTLET VENT | HHS9987 | HHS9988 | Steam | MOVDIG | FIP | 2" | 2" | Y globe valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 LTD | 2500 LTD | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23311 | 23.3 | 5247 | 2080_00005‐3
D | 01‐MOV‐HLS901 | LP FEEDWATER INLET STOP | HLS9102 | HLS9103 | Water | MOVDIG | FIP | 10" | 10" | Gate Valve | SA‐106 B | SA‐106 B | SA‐216 Gr WCB | 600 | 345 | 41.4 | 174 | 300 | 300 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 901 | 62 | 1 | Bypass Equalizer Type 4 | HP Valve | 2080_23302 | 23.3 | 5248 | 2080_00006‐1
D | 01‐MOV‐HLS907 | LP ECONOMIZER VENT | HLS9973 | HLS9974 | Water | MOVDIG | FIP | 2" | 2" | Gate Valve | SA‐106 B | SA‐106 B | SA‐105N | 600 | 489 | 41.4 | 253.8 | 1500 | 1500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 901 | 62 | 2 & 1 | ‐ | HP Valve | 2080_23306 | 23.3 | 5249 | 2080_00006‐1
D | 01‐YCV‐HHS902 | HP SH #1 DRAIN POT | HHS9305 | HBD9903 | Water | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 2741 | 1032 | 189 | 555.6 | 2500 | 2500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN/ CLOSED LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23314 | 23.3 | 5250 | 2080_00007‐1
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5251 | 2080_00003‐1
D | 01‐YCV‐HHS903 | HP ATTEMPERATOR LOOP DRAIN POT | HHS9307 | HBD9902 | Water | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2741 | 1032 | 189 | 555.6 | 2500 LTD | 2500 LTD | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN / CLOSE LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 4112 | 284 | 9 & 7 | ‐ | HP Valve | 2080_23313 | 23.3 | 5252 | 2080_00007‐1
D | 01‐YCV‐HIS905 | IP STEAM OUTLET DRAIN POT | HIS9927 | HBD9909 | Steam | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 1500 | 1500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 935 | 65 | 9 & 4 | ‐ | HP Valve | 2080_23312 | 23.3 | 5253 | 2080_00007‐1
D | 01‐YCV‐HIS906 | IP STEAM OUTLET DRAIN POT | HIS9933 | HBD9913 | Steam | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 624 | 622 | 43 | 327.6 | 1500 | 1500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 935 | 65 | 9 & 4 | ‐ | HP Valve | 2080_23327 | 23.3 | 5254 | 2080_00007‐1
D | 01‐YCV‐HLS909 | LP SUPERHEATER OUTLET DRAIN POT DRAIN | HLS9936 | HBD9912 | Water | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 624 | 9 | 328.7 | 1500 | 1500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN / CLOSE LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 196 | 14 | 9 & 2 | ‐ | HP Valve | 2080_23312 | 23.3 | 5255 | 2080_00007‐1
D | 01‐YCV‐HLS910 | LP SUPERHEATER OUTLET DRAIN | HLS9933 | HBD9923 | Water | POVPOS | FIP | 2" | 2" | Y globe valve | SA‐106 B | SA‐106 B | SA‐105N | 131 | 624 | 9 | 328.7 | 1500 | 1500 | SW | SW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN / CLOSE LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 196 | 14 | 9 & 2 | ‐ | HP Valve | 2080_23312 | 23.3 | 5256 | 2080_00007‐1
D | 01‐YCV‐HRS905 | REHEAT ATTEMPERATOR LOOP DRAIN POT | HRS9945 | HBD9908 | Water | POVPOS | FIP | 2 1/2" | 2 1/2" | Y globe valve | SA‐335 P22 | SA‐335 P22 | SA‐182 F22 | 624 | 946 | 43 | 508 | 1500 | 1500 | BW | BW | Pneumatic Actuator w/Handwheel HART 4‐20 mA Positioner & 4‐20 mA Position Transmitter OPEN / CLOSE LIMIT SWITCHES Positioning Operation, Fail Close Nema 4 Equipment & Junction Box 5‐10 sec. Open/Close Travel time 60‐120 PSIG Instrument Air Filter/Reducer air Set, SS Tubing & Fittings INCHING | 935 | 65 | 9 & 5 | ‐ | HP Valve | 2080_23330 | 23.3 | 5257 | 2080_00007‐1
D | 01‐YTS‐HLS995 | LP SPARGING STEAM STRAINER | HLS9178 | HLS9178 | Steam | NA | NA | 3" | 3" | Y‐Type Strainer | SA‐106 B | SA‐106 B | SA‐105 | 162 | 372 | 11.2 | 188.7 | 2500 | 2500 | BW | BW | Mesh Size 40 and 1" SW blowdown connection | 196 | 14 | 2 | ‐ | HP Valve | 2080_23702 | 23.33 | 5257 | 2080_00003‐1
D | 01‐YTS‐HIS995 | IP SPARGING STEAM STRAINER | HIS9107 | HIS9107 | Steam | NA | NA | 3" | 3" | Y‐Type Strainer | SA‐106 B | SA‐106 B | SA‐105 | 656 | 498 | 45.2 | 259 | 2500 | 2500 | BW | BW | Mesh Size 40 and 1" SW blowdown connection | 935 | 65 | 4 | ‐ | HP Valve | 2080_23701 | 23.33 | 5257 | 2080_00004‐2
D | 01‐YTS‐HRS901 | RHT ATTEMPERATOR SPRAY WATER STRAINER | HRS9176 | HRS9176 | Water | NA | NA | 2 1/2" | 2 1/2" | Y‐Type Strainer | SA‐106 B | SA‐106 B | SA‐105 | 624 | 1096 | 43 | 591.1 | 2500 | 2500 | BW | BW | Mesh Size 100 and 1" SW blowdown connection | 935 | 65 | 5 | ‐ | HP Valve | 2080_23652 | 23.33 | 5257 | 2080_00004‐4
D | 01‐YTS‐HHS995 | HP SPARGING STEAM STRAINER | HHS9221 | HHS9221 | Steam | NA | NA | 4" | 4" | Y‐Type Strainer | SA‐106 B | SA‐106 B | SA‐105 | 2773 | 684 | 191.2 | 362.4 | 1500 SPL | 1500 SPL | BW | BW | Mesh Size 40 and 1" SW blowdown connection | 4112 | 284 | 7 | ‐ | HP Valve | 2080_23653 | 23.33 | 5257 | 2080_00005‐2
D | 01‐YTS‐HHS901 | HP ATTEMPERATOR SPRAY WATER STRAINER | HHS9196 | HHS9196 | Water | NA | NA | 2 1/2" | 2 1/2" | Y‐Type Strainer | SA‐106 C | SA‐106 C | SA‐105 | 4100 | 374 | 282.7 | 189.9 | 2500 | 2500 | BW | BW | Mesh Size 100 and 1" SW blowdown connection | 6150 | 424 | 6 | ‐ | HP Valve | 2080_23651 | 23.33 | 5257 | 2080_00005‐3
D | 01‐MOV‐HLS902 | LP SUPERHEATER OUTLET VENT | HLS9987 | HLS9988 | Steam | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 131 | 623 | 9 | 328.5 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 196 | 14 | 2 | ‐ | ValvTechnologies | 2080_23619 | 23.36 | 5257 | 2080_00003‐2
D | 01‐MOV‐HIS902 | IP SUPERHEATER OUTLET VENT | HIS9966 | HIS9966 | Steam | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 624 | 622 | 43 | 327.6 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23616 | 23.36 | 5257 | 2080_00004‐3
D | 01‐MOV‐HRS911 | REHEAT VENT | HRS9973 | HRS9973 | Steam | MOVDIG | FIP | 4" | 4" | Ball valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 1096 | 43 | 591.1 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 5 | ‐ | ValvTechnologies | 2080_23621 | 23.36 | 5257 | 2080_00004‐4
D | 01‐MOV‐HHS903 | HP CASCADING BLOW DOWN ISOLATION | HHS9943 | HHS9943 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 2773 | 684 | 191.2 | 362.4 | 2500 | 2500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23611 | 23.36 | 5257 | 2080_00005‐2
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5257 | 2080_00003‐1
D | 01‐MOV‐HHS905 | HP SUPERHEATER OUTLET VENT | HHS9986 | HHS9987 | Steam | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2534 | 1098 | 174.7 | 592 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23610 | 23.36 | 5257 | 2080_00005‐3
D | 01‐MOV‐HBD901 | HP BD MANIFOLD DRAIN | HBD9915 | HBD9916 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 58 | 750 | 4 | 399 | 150 | 150 | SW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 78 | 5 | 9 | ‐ | ValvTechnologies | 2080_23603 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HBD902 | IP BD MANIFOLD DRAIN | HBD9917 | HBD9918 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 58 | 750 | 4 | 399 | 150 | 150 | SW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 78 | 5 | 9 | ‐ | ValvTechnologies | 2080_23604 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HBD903 | LP BD MANIFOLD DRAIN | HBD9919 | HBD9921 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 58 | 750 | 4 | 399 | 150 | 150 | SW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 78 | 5 | 9 | ‐ | ValvTechnologies | 2080_23605 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HHS909 | HP INTERMITTENT BLOWDOWN STOP | HHS9947 | HHS9947 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23606 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HHS910 | HP SH #1 DRAIN POT STOP | HHS9305 | HHS9305 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 2741 | 683 | 189 | 361.5 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23608 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HHS911 | HP ATTEMPERATOR DRAIN POT STOP | HHS9307 | HHS9307 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 2741 | 1032 | 189 | 555.6 | 2500 | 2500 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23609 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HHS912 | HP INTERMITTENT BLOWDOWN STOP | HHS9945 | HHS9945 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 C | SA‐106 C | SA‐105 | 2998 | 696 | 206.7 | 368.9 | 2500 | 2500 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 4112 | 284 | 7 | ‐ | ValvTechnologies | 2080_23607 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HIS905 | IP CONTINUOUS BLOWDOWN STOP | HIS9912 | HIS9912 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 656 | 498 | 45.2 | 259 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23617 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HIS915 | IP DRAIN POT STOP | HIS9927 | HIS9927 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 624 | 622 | 43 | 327.6 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23614 | 23.36 | 5257 | 2080_00007‐1
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5257 | 2080_00003‐1
D | 01‐MOV‐HIS916 | IP INTERMITTENT BLOWDOWN STOP | HIS9914 | HIS9914 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 812 | 522 | 56 | 272.2 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23612 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HIS917 | IP INTERMITTENT BLOWDOWN STOP | HIS9916 | HIS9916 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 812 | 522 | 56 | 272.2 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23613 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HIS918 | IP OUTLET DRAIN POT STOP | HIS9933 | HIS9933 | Water | MOVDIG | FIP | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 624 | 622 | 43 | 327.6 | 600 | 600 | SW | SW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 4 | ‐ | ValvTechnologies | 2080_23615 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HLS908 | LP INTERMITTENT BLOWDOWN STOP | HLS9934 | HLS9934 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 196 | 386 | 13.5 | 196.5 | 150 | 150 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 196 | 14 | 2 | ‐ | ValvTechnologies | 2080_23618 | 23.36 | 5257 | 2080_00007‐1
D | 01‐MOV‐HRS914 | REHEAT ATTEMPERATOR LOOP DRAIN POT | HRS9945 | HRS9945 | Water | MOVDIG | FIP | 2 1/2" | 2 1/2" | Ball valve | SA‐335 P91 | SA‐335 P91 | SA‐182 F91 | 624 | 946 | 43 | 508 | 600 | 600 | BW | BW | Electric Actuator with Hand Wheel 460/3/60 VAC Intergal Motor Starter Local/Remote Selector Switch Local Open /Close Pushbuttons Open/Close Limit Switches Open/Close Torque Switches Nema 4 15 ‐ 45 sec.Open/Close Travel Time | 935 | 65 | 5 | ‐ | ValvTechnologies | 2080_23620 | 23.36 | 5257 | 2080_00007‐1
D | 01‐VHLS995 | LP DRAIN POT STOP | HLS9936 | HLS9936 | Water | NA | NA | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 131 | 624 | 9 | 328.7 | 300 | 300 | SW | SW |  | 196 | 14 | 2 | ‐ | ValvTechnologies | 2080_23601 | 23.36 | 5257 | 2080_00007‐1
D | 01‐VHLS996 | LP DRAIN POT STOP | HLS9933 | HLS9933 | Water | NA | NA | 2" | 2" | Ball valve | SA‐106 B | SA‐106 B | SA‐105 | 131 | 624 | 9 | 328.7 | 300 | 300 | SW | SW |  | 196 | 14 | 2 | ‐ | ValvTechnologies | 2080_23602 | 23.36 | 5257 | 2080_00007‐1
D | 01‐PRV‐HLS997 | LP DRUM PRESSURE RELIEF VALVE 1 | LP DRUM | HLS9705 | Steam | NA | NA | 4" | 6" | PRV | SA‐106 B | SA‐106 B | SA‐216 Gr WCC | 131 | 356 | 9 | 179.9 | 150 | 150 | FL | FL |  | 196 | 14 | 2 | ‐ | Trillium | 2080_23212 | 23.03 | 5257 | 2080_00003‐1