## First Sheet
Loc/Asset | Label | Last Response | Alarm Config | Condition | Response Date/Time | Response By | Comment | Active
ANSWER FIRST | Which Shift | Day |  | NORMAL | 07/11/2026 06:20:37 | Martinez, Geovanny
BOP | Units Running | Both |  | NORMAL | 07/11/2026 06:20:38 | Martinez, Geovanny
BOP | Is RO "A" running? | Yes |  | NORMAL | 07/11/2026 06:20:43 | Martinez, Geovanny
DEMINERALIZED WATER | Bag Filter DP A (<10) | 3.4 PSI | HI: > 10 PSI | NORMAL | 07/11/2026 06:20:49 | Martinez, Geovanny
DEMINERALIZED WATER | Cartridge Filter DP A (<10) | 2.1 PSI | HI: > 10 PSI | NORMAL | 07/11/2026 06:20:57 | Martinez, Geovanny
DEMINERALIZED WATER | Interstage pH in range? (9-10) | No | HI: <> Yes | NORMAL | 07/11/2026 06:21:11 | Martinez, Geovanny | 8.92
DEMINERALIZED WATER | RO "A" has no alarms and in auto. | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:21:28 | Martinez, Geovanny
DEMINERALIZED WATER | Is RO "B" running? | No |  | NORMAL | 07/11/2026 06:21:53 | Martinez, Geovanny
DEMINERALIZED WATER | Bag filter DP (<10) | .78 Psi | HI: > 10 Psi | NORMAL | 07/08/2026 05:31:33 | Silva, Juan
DEMINERALIZED WATER | Cartridge Filter DP (<10) | 1.43 Psi | HI: > 10 Psi | NORMAL | 07/08/2026 05:31:36 | Silva, Juan
DEMINERALIZED WATER | Interstage pH is in range (9-10) | Yes | HI: <> Yes | NORMAL | 07/08/2026 05:31:39 | Silva, Juan
DEMINERALIZED WATER | RO "B" has no alarms and in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:21:54 | Martinez, Geovanny
DEMINERALIZED WATER | Chem Tank Level - Sodium Bisulfite | 40 % | HI: < 25 % | NORMAL | 07/11/2026 06:22:56 | Martinez, Geovanny
DEMINERALIZED WATER | Chem Tank Level - Caustic | 20 % | HI: < 25 % | PENDING | 07/11/2026 06:22:59 | Martinez, Geovanny
DEMINERALIZED WATER | Chem Tank Level - Anti Scalant | 60 % | HI: < 25 % | NORMAL | 07/11/2026 06:23:07 | Martinez, Geovanny
DEMINERALIZED WATER | Chem Tank Level - Sodium Hypochlorite | 90 % | HI: < 25 % | NORMAL | 07/11/2026 06:23:29 | Martinez, Geovanny
DEMINERALIZED WATER | Draw Down - Sodium Bisulfite | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:23:31 | Martinez, Geovanny
DEMINERALIZED WATER | Draw Down - Caustic | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:23:31 | Martinez, Geovanny
DEMINERALIZED WATER | Draw Down - Anti Scalant | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:23:38 | Martinez, Geovanny
DEMINERALIZED WATER | Draw Down - Sodium Hypochlorite | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:23:39 | Martinez, Geovanny
DEMINERALIZED WATER | Demin Forwarding Pump Oil Level | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:23:39 | Martinez, Geovanny
DEMINERALIZED WATER | Demin Tank Heater (38-100 F) | 77 Deg F | HI: > 100 Deg F LO: < 38 Deg F | NORMAL | 07/11/2026 06:27:00 | Martinez, Geovanny
SERVICE WATER | Pump Oil Level | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:26:19 | Martinez, Geovanny
SERVICE WATER | Suction Pressure (>14) | 13 | LO: < 5 | NORMAL | 07/11/2026 06:26:19 | Martinez, Geovanny
SERVICE WATER | Discharge Pressure (>65) | 200 |  | NORMAL | 07/11/2026 06:26:19 | Martinez, Geovanny
SERVICE WATER | Pump Vibration and Noises | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:26:20 | Martinez, Geovanny
SERVICE WATER | Tank Heater Temp (40-100 F) | 73 Deg F | HI: > 100 Deg F LO: < 40 Deg F | NORMAL | 07/11/2026 06:26:23 | Martinez, Geovanny
SERVICE WATER | Free Chlorine Analyzer Reading | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:26:24 | Martinez, Geovanny
FIRE PROTECTION SYSTEM | Check Local Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:27:06 | Martinez, Geovanny
FIRE PROTECTION SYSTEM | Header Pressure (155-180 PSI) | 157 PSI | HI: > 180 PSI LO: < 155 PSI | NORMAL | 07/11/2026 06:27:08 | Martinez, Geovanny
FIRE PROTECTION SYSTEM | Diesel Tank Level (>75%) | 90 % | LO: < 75 % | NORMAL | 07/11/2026 06:28:06 | Martinez, Geovanny
SPARE GSU TRANSFORMER (00-XFMR) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 06:28:08 | Martinez, Geovanny
AMMONIA | Pump Disch Press. (80-100 PSI) | 90 PSI | HI: > 100 PSI LO: < 80 PSI | NORMAL | 07/11/2026 07:15:52 | Martinez, Geovanny
AMMONIA | Ammonia Tank Level SG North | 89 | LO: < 40 | NORMAL | 07/11/2026 07:15:34 | Martinez, Geovanny
AMMONIA | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 07:15:34 | Martinez, Geovanny
AMMONIA | Ammonia Tank Level SG South | 31 | LO: < 40 | NORMAL | 07/11/2026 07:15:37 | Martinez, Geovanny
AUXILIARY BOILER | FW Pump Oil Levels | Sat | HI: = Unsat | NORMAL | 07/11/2026 07:15:54 | Martinez, Geovanny
AUXILIARY BOILER | Chem Tank Level/Draw Down | Sat | HI: = Unsat | NORMAL | 07/11/2026 07:15:54 | Martinez, Geovanny
AUXILIARY BOILER | Loovers/Building Heaters (Winter) | Sat | HI: = Unsat | NORMAL | 07/11/2026 07:15:55 | Martinez, Geovanny
AUXILIARY BOILER | Check Local PLC/Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 07:15:55 | Martinez, Geovanny
WASTE WATER SUMP (00-WDR-SMP-01) | Check Display for Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 07:15:57 | Martinez, Geovanny
WASTE WATER SUMP (00-WDR-SMP-01) | Air Curtain Set Flow/Pressure | Sat | HI: = Unsat | NORMAL | 07/11/2026 07:15:57 | Martinez, Geovanny
AIR COMPRESSOR 1A (00-INA-CMP-01A) | AIR COMPRESSOR STATUS | LEAD |  | NORMAL | 07/11/2026 09:33:45 | Martinez, Geovanny
AIR COMPRESSOR 1A (00-INA-CMP-01A) | Alarms | No |  | NORMAL | 07/11/2026 09:33:45 | Martinez, Geovanny
AIR DRYER 1A (00-INA-ADY-01A) | Dew Point | -97 | LO: > -40 | NORMAL | 07/11/2026 09:33:49 | Martinez, Geovanny
AIR COMPRESSOR 1B (00-INA-CMP-01B) | AIR COMPRESSOR STATUS. | OFF |  | NORMAL | 07/11/2026 09:34:07 | Martinez, Geovanny
AIR COMPRESSOR 1B (00-INA-CMP-01B) | Alarms | No | HI: = Yes | NORMAL | 07/11/2026 09:34:08 | Martinez, Geovanny
AIR DRYER 1B (00-INA-ADY-01B) | Dew Point | -103 | LO: > -40 | NORMAL | 07/11/2026 09:34:09 | Martinez, Geovanny
INSTRUMENT AIR | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:34:09 | Martinez, Geovanny
INSTRUMENT AIR | Test Solenoid on Wet and Dry Tanks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:34:11 | Martinez, Geovanny
HYDROGEN TRAILERS (HYDROGENTRAILERS) | Main Header Pressure | 2450 | LO: < 250 | NORMAL | 07/11/2026 09:35:35 | Martinez, Geovanny
HYDROGEN TRAILERS (HYDROGENTRAILERS) | Trailer in Service | East |  | NORMAL | 07/11/2026 09:35:43 | Martinez, Geovanny
BOP | Is Standby Trailer full and available? | No |  | NORMAL | 07/11/2026 09:35:45 | Martinez, Geovanny
NITROGEN GENERATOR SKID (00-FGS-SKD-13) | Active alarms (North Unit) | Sat | HI: = Unsat | NORMAL | 07/11/2026 07:16:00 | Martinez, Geovanny
NITROGEN GENERATOR SKID (00-FGS-SKD-13) | North Unit Running | Yes |  | NORMAL | 07/11/2026 07:16:00 | Martinez, Geovanny
NITROGEN GENERATOR SKID (00-FGS-SKD-13) | North Unit in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:16:04 | Martinez, Geovanny
NITROGEN GENERATOR SKID (00-FGS-SKD-13) | Active alarms (South Unit) | Sat |  | NORMAL | 07/11/2026 07:16:05 | Martinez, Geovanny
NITROGEN GENERATOR SKID (00-FGS-SKD-13) | South Unit Running | No |  | NORMAL | 07/11/2026 07:16:07 | Martinez, Geovanny
NITROGEN GENERATOR SKID (00-FGS-SKD-13) | South Unit in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:16:08 | Martinez, Geovanny
FUEL GAS COMPRESSOR (00-FGS-CMP-01A) | Motor Oil Flow | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:35:55 | Martinez, Geovanny
FUEL GAS COMPRESSOR (00-FGS-CMP-01A) | Check Display for Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:35:55 | Martinez, Geovanny
FUEL GAS COMPRESSOR (00-FGS-CMP-01A) | Enclosure Pressure Ok | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:35:55 | Martinez, Geovanny
FUEL GAS COMPRESSOR (00-FGS-CMP-01A) | ACHE Noise and Vibrations | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:35:55 | Martinez, Geovanny
FUEL GAS COMPRESSOR (00-FGS-CMP-01A) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:35:56 | Martinez, Geovanny
FUEL GAS CHROMATOGRAPH (00-FGS-FLG-11) | Vent Fan On/Build Temp | Sat |  | NORMAL | 07/11/2026 09:35:57 | Martinez, Geovanny
FUEL GAS CHROMATOGRAPH (00-FGS-FLG-11) | Check Panel for Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:35:57 | Martinez, Geovanny
GLYCOL/WATER RECIRCULATION PUMP SKID (00-FGS-SKD-06) | Bladder Tank Desiccant color (White is normal) | Sat | HI: <> Sat | NORMAL | 07/11/2026 09:35:58 | Martinez, Geovanny
GLYCOL/WATER RECIRCULATION PUMP SKID (00-FGS-SKD-06) | Which pump is running | South |  | NORMAL | 07/11/2026 09:35:59 | Martinez, Geovanny
GLYCOL/WATER RECIRCULATION PUMP SKID (00-FGS-SKD-06) | DP across Inlet Strainer of the running pump | 1.4 |  | NORMAL | 07/11/2026 09:35:59 | Martinez, Geovanny
GLYCOL HEATER | Active Alarms | No | HI: <> No | NORMAL | 07/11/2026 09:35:59 | Martinez, Geovanny
GLYCOL HEATER | Abnormal Conditions/Leaks | Sat | HI: <> Sat | NORMAL | 07/11/2026 09:36:01 | Martinez, Geovanny
LP ELECTRIC HEATER (00-FGS-SKD-11) | Fuel Gas Outlet Temperature | 109 |  | NORMAL | 07/11/2026 09:36:02 | Martinez, Geovanny
LP ELECTRIC HEATER (00-FGS-SKD-11) | Check Control Panel/Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:36:03 | Martinez, Geovanny
LP ELECTRIC HEATER (00-FGS-SKD-11) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:36:03 | Martinez, Geovanny
GAS TURBINE FUEL GAS CARTRIDGE FILTER 01-FGS-FLT-01 (01-FGS-FLT-01) | SG Level on Bottom of Main Tank | 0 |  | NORMAL | 07/11/2026 09:36:05 | Martinez, Geovanny
GAS TURBINE FUEL GAS CARTRIDGE FILTER 01-FGS-FLT-01 (01-FGS-FLT-01) | SG on Drip Tank | 0 |  | NORMAL | 07/11/2026 09:36:05 | Martinez, Geovanny
EDG (01-EDG) | Display Check | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:36:08 | Martinez, Geovanny
EDG (01-EDG) | Fuel Level (>90%) | 75 | LO: < 90 | NORMAL | 07/11/2026 09:36:09 | Martinez, Geovanny
EMERGENCY DIESEL GENERATOR | Fuel tank free of any visible damage? | Yes |  | NORMAL | 07/11/2026 09:36:10 | Martinez, Geovanny
EDG (01-EDG) | Check for Leaks/Abnormal Conditions | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:36:11 | Martinez, Geovanny
EDG (01-EDG) | Battery Charger Status | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:36:12 | Martinez, Geovanny
EDG (01-EDG) | Switch in Auto | Yes | HI: = No | NORMAL | 07/11/2026 09:36:13 | Martinez, Geovanny
MEDIUM VOLTAGE SYSTEM | Check UPS Panel | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:36:55 | Martinez, Geovanny
MEDIUM VOLTAGE SYSTEM | Main Dc panel Volts | 129.7 Volts |  | NORMAL | 07/11/2026 09:37:30 | Martinez, Geovanny
MEDIUM VOLTAGE SYSTEM | Main DC Panel Amps | -.5 Amps |  | NORMAL | 07/11/2026 09:37:37 | Martinez, Geovanny
MEDIUM VOLTAGE SYSTEM | Batt Chargers Volts A (130.5 VDC) | 130.1 VDC |  | NORMAL | 07/11/2026 09:37:38 | Martinez, Geovanny
MEDIUM VOLTAGE SYSTEM | Batt Charger Volts B (130.5 VDC) | 130.1 VDC |  | NORMAL | 07/11/2026 09:37:38 | Martinez, Geovanny
MEDIUM VOLTAGE SYSTEM | U1 Battery Room Temperature | 67 |  | NORMAL | 07/11/2026 09:37:04 | Martinez, Geovanny
MEDIUM VOLTAGE SYSTEM | U2 Battery Room Temperature | 67 |  | NORMAL | 07/11/2026 09:37:06 | Martinez, Geovanny
MEDIUM VOLTAGE SYSTEM | Building Temperature | 76 |  | NORMAL | 07/11/2026 09:37:27 | Martinez, Geovanny
UNIT 1 OUTFALL (01-OUTFALL) | Effluent Clear of Debris or no flow | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:37:44 | Martinez, Geovanny
UNIT 1 OUTFALL (01-OUTFALL) | Check for color or odors or no flow | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:37:44 | Martinez, Geovanny
BOP | Is the north storage containment being used? | Yes |  | NORMAL | 07/11/2026 09:37:45 | Martinez, Geovanny
BOP | Is there water level? | No |  | NORMAL | 07/11/2026 09:37:46 | Martinez, Geovanny
BOP | Is there evidence of oil in the containment? | No | HI: IN Yes | NORMAL | 07/09/2026 01:01:43 | Stroud, Andrew
BOP | Was water pumped down? | Yes | HI: IN No | NORMAL | 07/09/2026 01:02:16 | Stroud, Andrew