## First Sheet
Loc/Asset | Label | Last Response | Alarm Config | Condition | Response Date/Time | Response By | Comment | Active
Control Room Checks | Any of the units on? | Yes |  | NORMAL | 07/11/2026 06:25:17 | Mykhailenko, Eugene
Control Room Checks | Day Ahead Gas Burn Sent | Yes |  | NORMAL | 07/11/2026 06:28:03 | Mykhailenko, Eugene
Control Room Checks | Review Log Book for TOI-TMOD (forced logic). | Yes |  | NORMAL | 07/11/2026 06:28:16 | Mykhailenko, Eugene
Control Room Checks | Check Point Review for points Off Scan on all units. | Yes |  | NORMAL | 07/11/2026 06:28:18 | Mykhailenko, Eugene
Control Room Checks | Security cameras and front gate operational and outside security checks complete. | Yes |  | NORMAL | 07/11/2026 06:28:20 | Mykhailenko, Eugene
Control Room Checks | Check that AED has a green light indication | Yes |  | NORMAL | 07/11/2026 06:28:22 | Mykhailenko, Eugene
Service Water | Service water pump running | A |  | NORMAL | 07/11/2026 06:28:47 | Mykhailenko, Eugene
Service Water | Diesel/Electric/Jokey fire pumps running | No |  | NORMAL | 07/11/2026 06:28:49 | Mykhailenko, Eugene
Service Water | Service water level | 33.1 |  | NORMAL | 07/11/2026 06:28:59 | Mykhailenko, Eugene
Service Water | Free Chlorine reading | 0.088 |  | NORMAL | 07/11/2026 06:29:12 | Mykhailenko, Eugene
Demin Water | Demin Water Tank Level | 33.9 |  | NORMAL | 07/11/2026 06:29:27 | Mykhailenko, Eugene
Demin Water | Demin makeup to Tank YV-DWT115 in AUTO | Yes |  | NORMAL | 07/11/2026 06:29:30 | Mykhailenko, Eugene
Demin Water | Demin Dump to Water treatment sump YV--DWT125 AUTO | Yes |  | NORMAL | 07/11/2026 06:29:33 | Mykhailenko, Eugene
Demin Water | Demin water pumps running | A |  | NORMAL | 07/11/2026 06:29:36 | Mykhailenko, Eugene
Demin Water | Demin Silica Final pbb (Must be < 10) | 5.32 ppb |  | NORMAL | 07/11/2026 06:29:50 | Mykhailenko, Eugene
Control air | AIR COMPRESSORS RUNNING | A |  | NORMAL | 07/11/2026 06:30:12 | Mykhailenko, Eugene
Control air | PLANT AIR pressure | 116 PSIG |  | NORMAL | 07/11/2026 06:30:26 | Mykhailenko, Eugene
SCR ammonia tanks | NORTH TANK LEVEL | 36 INCHES |  | NORMAL | 07/11/2026 06:30:43 | Mykhailenko, Eugene
SCR ammonia tanks | SOUTH TANK LEVEL | 101 INCNES |  | NORMAL | 07/11/2026 06:30:45 | Mykhailenko, Eugene
SCR ammonia tanks | Aqueos ammonia pump running | A |  | NORMAL | 07/11/2026 06:30:47 | Mykhailenko, Eugene
Fuel Gas System | FGC running | C; A |  | NORMAL | 07/11/2026 06:31:01 | Mykhailenko, Eugene
Fuel Gas System | FGC setpoint | 760/750 Psig |  | NORMAL | 07/11/2026 06:31:02 | Mykhailenko, Eugene
Electrical checks | 13.8 kv SWGR feed breaker that is open | 52-T |  | NORMAL | 07/11/2026 06:31:21 | Mykhailenko, Eugene
Electrical checks | 6.9KV SWGR feed breaker that is OPEN | 52-T |  | NORMAL | 07/11/2026 06:31:33 | Mykhailenko, Eugene
Electrical checks | EDG black out mode selected | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:31:48 | Mykhailenko, Eugene
Electrical checks | Any active alarms on electrical systems | No | HI: <> No | NORMAL | 07/11/2026 06:31:58 | Mykhailenko, Eugene
Electrical checks | U1 Line Voltage | 353 kV | HI: > 357 kV LO: < 347 kV | NORMAL | 07/11/2026 06:32:07 | Mykhailenko, Eugene
Electrical checks | U2 Line Voltage | 352 kV | HI: > 357 kV LO: < 347 kV | NORMAL | 07/11/2026 06:32:10 | Mykhailenko, Eugene
CEMS checks | CEMS cals passed | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:32:15 | Mykhailenko, Eugene
Auxiliary Steam | Aux Boiler | Off |  | NORMAL | 07/11/2026 06:32:31 | Mykhailenko, Eugene
Auxiliary Steam | Aux boiler available and ready for start | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:32:52 | Mykhailenko, Eugene
Control Room Checks | Unit 1 | On;\ |  | NORMAL | 07/11/2026 06:33:03 | Mykhailenko, Eugene
Control Room Checks | Unit 2 | On;\ |  | NORMAL | 07/11/2026 06:33:13 | Mykhailenko, Eugene
HP Bypass system | HP Stm Bypass to CRH PCV-HPS100 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:33:43 | Mykhailenko, Eugene
HP Bypass system | HP Stm Bypass Desup Block YV-BFW715 & TCV-BFW716 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:33:52 | Mykhailenko, Eugene
HP Bypass system | HP Bypass Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:34:01 | Mykhailenko, Eugene
HP Bypass system | HP Superheater Byp CTRL VLV PCV-HHS903 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:34:14 | Mykhailenko, Eugene
HP Bypass system | HP Steam Terminal Block YV-BFW705 & TCV-BFW706 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:34:18 | Mykhailenko, Eugene
HP Bypass system | HP Terminal Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:34:19 | Mykhailenko, Eugene
HRH Bypass system | HRH Stm Bypass to ACC PCV-HRH100 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:34:54 | Mykhailenko, Eugene
HRH Bypass system | HRH Stm Bypass Desup Block YV-CND702 & TCV-CND707 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:34:58 | Mykhailenko, Eugene
HRH Bypass system | HRH Bypass Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:35:01 | Mykhailenko, Eugene
HRH Bypass system | HRH Steam Terminal Block YV-BFW735 & TCV-BFW736 in Auto and temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:35:03 | Mykhailenko, Eugene
HRH Bypass system | HRH Terminal Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:35:05 | Mykhailenko, Eugene
LP Bypass system | LP Stm Bypass to ACC PCV-LPS100 | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:35:23 | Mykhailenko, Eugene
LP Bypass system | LP Stm Bypass Desup Block YV-CND725 & TCV-CND726 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:35:25 | Mykhailenko, Eugene
LP Bypass system | LP Bypass Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:35:26 | Mykhailenko, Eugene
HP Bypass system | HP Stm Bypass to CRH PCV-HPS100 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:11 | Mykhailenko, Eugene
HP Bypass system | HP Stm Bypass Desup Block YV-BFW715 & TCV-BFW716 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:17 | Mykhailenko, Eugene
HP Bypass system | HP Bypass Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:21 | Mykhailenko, Eugene
HP Bypass system | HP Superheater Byp CTRL VLV PCV-HHS903 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:27 | Mykhailenko, Eugene
HP Bypass system | HP Steam Terminal Block YV-BFW705 & TCV-BFW706 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:29 | Mykhailenko, Eugene
HP Bypass system | HP Terminal Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:31 | Mykhailenko, Eugene
HRH Bypass system | HRH Stm Bypass to ACC PCV-HRH100 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:41 | Mykhailenko, Eugene
HRH Bypass system | HRH Stm Bypass Desup Block YV-CND702 & TCV-CND707 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:43 | Mykhailenko, Eugene
HRH Bypass system | HRH Bypass Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:45 | Mykhailenko, Eugene
HRH Bypass system | HRH Steam Terminal Block YV-BFW735 & TCV-BFW736 in Auto and temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:49 | Mykhailenko, Eugene
HRH Bypass system | HRH Terminal Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:39:51 | Mykhailenko, Eugene
LP Bypass system | LP Stm Bypass to ACC PCV-LPS100 | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:40:30 | Mykhailenko, Eugene
LP Bypass system | LP Stm Bypass Desup Block YV-CND725 & TCV-CND726 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:40:34 | Mykhailenko, Eugene
LP Bypass system | LP Bypass Desup Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:40:36 | Mykhailenko, Eugene
HP steam System | HP Drum Level Control LCV-HHS932 & HHS921 in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:41:29 | Mykhailenko, Eugene
HP steam System | HP Drum Level Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:41:32 | Mykhailenko, Eugene
HP steam System | HP Feedwater Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:41:41 | Mykhailenko, Eugene
HP steam System | HP IBD Drum CV YCV-HHS901 | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:41:43 | Mykhailenko, Eugene
HP steam System | HP continues BD MOV-HHS943 | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:41:46 | Mykhailenko, Eugene
HP steam System | HP Interstage Attemperator TCV-HHS801 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:42:06 | Mykhailenko, Eugene
HP steam System | HP Interstage Attemp Block Valve MOV-HHS908 in Auto | No | HI: <> Yes | PENDING | 07/11/2026 06:42:08 | Mykhailenko, Eugene | TMOD
HP steam System | HP Drum Level Control LCV-HHS932 & HHS921 in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:43:04 | Mykhailenko, Eugene
HP steam System | HP Drum Level Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:43:27 | Mykhailenko, Eugene
HP steam System | HP Feedwater Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:43:29 | Mykhailenko, Eugene
HP steam System | HP IBD Drum CV YCV-HHS901 | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:43:39 | Mykhailenko, Eugene
HP steam System | HP continues BD MOV-HHS943 | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:43:43 | Mykhailenko, Eugene
HP steam System | HP Interstage Attemperator TCV-HHS801 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:43:45 | Mykhailenko, Eugene
HP steam System | HP Interstage Attemp Block Valve MOV-HHS908 in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:43:52 | Mykhailenko, Eugene
IP Steam System | IP Drum Level Control LCV-HIS931 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:46:57 | Mykhailenko, Eugene
IP Steam System | IP Drum Level Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:47:10 | Mykhailenko, Eugene
IP Steam System | IP Feedwater Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:47:18 | Mykhailenko, Eugene
IP Steam System | IP IBD Drum CV YCV-HIS901 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:47:22 | Mykhailenko, Eugene
IP Steam System | IP continues BD MOV-HIS905 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:47:30 | Mykhailenko, Eugene
IP Steam System | IP Steam Header PCV-HIS903 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:47:38 | Mykhailenko, Eugene
IP Steam System | RH Interstage Attemperator TCV-HRS901 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:47:40 | Mykhailenko, Eugene
IP Steam System | RH Interstage Attemperator MOV-HRS912 in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:47:44 | Mykhailenko, Eugene
IP Steam System | IP Drum Level Control LCV-HIS931 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:48:01 | Mykhailenko, Eugene
IP Steam System | IP Drum Level Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:48:16 | Mykhailenko, Eugene
IP Steam System | IP Feedwater Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:48:23 | Mykhailenko, Eugene
IP Steam System | IP IBD Drum CV YCV-HIS901 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:48:25 | Mykhailenko, Eugene
IP Steam System | IP continues BD MOV-HIS905 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:48:28 | Mykhailenko, Eugene
IP Steam System | IP Steam Header PCV-HIS903 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:48:32 | Mykhailenko, Eugene
IP Steam System | RH Interstage Attemperator TCV-HRS901 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:48:40 | Mykhailenko, Eugene
IP Steam System | RH Interstage Attemperator MOV-HRS912 in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:48:42 | Mykhailenko, Eugene
LP Steam System | LP Drum Level Control LCV-HLS921 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:49:48 | Mykhailenko, Eugene
LP Steam System | LP Drum Level Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:49:52 | Mykhailenko, Eugene
LP Steam System | LP Feedwater Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:50:02 | Mykhailenko, Eugene
LP Steam System | LP IBD Drum Block MOV-HLS908 & CV YCV-HLS901 | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:50:04 | Mykhailenko, Eugene
LP Steam System | LP Drum Level Control LCV-HLS921 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:50:21 | Mykhailenko, Eugene
LP Steam System | LP Drum Level Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:50:22 | Mykhailenko, Eugene
LP Steam System | LP Feedwater Flow Transmitters All in Service and Reading Correctly | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:50:26 | Mykhailenko, Eugene
LP Steam System | LP IBD Drum Block MOV-HLS908 & CV YCV-HLS901 | Yes | HI: <> Yes | NORMAL | 07/11/2026 06:50:27 | Mykhailenko, Eugene
Duct Burner | U1 Duct Burner Blower Running | A |  | NORMAL | 07/11/2026 06:50:47 | Mykhailenko, Eugene
Duct Burner | U2 Duct Burner Blower Running | A |  | NORMAL | 07/11/2026 06:50:49 | Mykhailenko, Eugene
Cycle chemical feed | Ammonia Pump Running | A |  | NORMAL | 07/11/2026 06:59:50 | Mykhailenko, Eugene
Cycle chemical feed | Cond After Chem Feed | 19 us/m | HI: > 23 us/m LO: < 18 us/m | NORMAL | 07/11/2026 06:59:57 | Mykhailenko, Eugene
Cycle chemical feed | Active Alarms | No | HI: <> No | NORMAL | 07/11/2026 06:59:59 | Mykhailenko, Eugene
Cycle chemical feed | Ammonia Pump Running | A |  | NORMAL | 07/11/2026 07:00:18 | Mykhailenko, Eugene
Cycle chemical feed | Cond After Chem Feed | 19.7 us/m | HI: > 23 us/m LO: < 18 us/m | NORMAL | 07/11/2026 07:00:56 | Mykhailenko, Eugene
Cycle chemical feed | Active Alarms | No | HI: <> No | NORMAL | 07/11/2026 07:00:57 | Mykhailenko, Eugene
SCR ammonia injection system | NH3 Flow Cntrl FCV-AQA803 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:02:34 | Mykhailenko, Eugene
SCR ammonia injection system | NH3 Flow Cntrl FCV-AQA803 Flow | 985 LB/H |  | NORMAL | 07/11/2026 07:02:52 | Mykhailenko, Eugene
SCR ammonia injection system | Exhaust Gas Blowers Running | B |  | NORMAL | 07/11/2026 07:02:55 | Mykhailenko, Eugene
SCR ammonia injection system | Dilution Air Heater Running | B |  | NORMAL | 07/11/2026 07:02:56 | Mykhailenko, Eugene
SCR ammonia injection system | Dilution Air Heater Temperature | 663 F |  | NORMAL | 07/11/2026 07:02:59 | Mykhailenko, Eugene
SCR ammonia injection system | NH3 Flow Cntrl FCV-AQA803 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:03:10 | Mykhailenko, Eugene
SCR ammonia injection system | NH3 Flow Cntrl FCV-AQA803 Flow | 1130 LB/H |  | NORMAL | 07/11/2026 07:03:25 | Mykhailenko, Eugene
SCR ammonia injection system | Exhaust Gas Blowers Running | A |  | NORMAL | 07/11/2026 07:03:41 | Mykhailenko, Eugene
SCR ammonia injection system | Dilution Air Heater Running | A |  | NORMAL | 07/11/2026 07:03:42 | Mykhailenko, Eugene
SCR ammonia injection system | Dilution Air Heater Temperature | 662 F |  | NORMAL | 07/11/2026 07:03:56 | Mykhailenko, Eugene
Boiler Feed Water System | Boiler Feedwater Pump Running | B |  | NORMAL | 07/11/2026 07:04:09 | Mykhailenko, Eugene
Boiler Feed Water System | Lube Oil Temp of online BFWP (Highest) | 122 deg F | HI: > 146 deg F | NORMAL | 07/11/2026 07:04:41 | Mykhailenko, Eugene
Boiler Feed Water System | Standby BFWP in Auto | Yes |  | NORMAL | 07/11/2026 07:04:44 | Mykhailenko, Eugene
Boiler Feed Water System | Offline BFWP Lube oil pump running | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:04:45 | Mykhailenko, Eugene
Boiler Feed Water System | 01A BFP Min Flow recirc FCV-BFW147, IP discharge MOV-BFW139/140, HP discharge MOV-BFW145/146 are in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:04:47 | Mykhailenko, Eugene
Boiler Feed Water System | 01B BFP Min Flow recirc FCV-BFW187, IP discharge MOV-BFW179/80, HP discharge MOV-BFW185/186 are in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:04:47 | Mykhailenko, Eugene
Boiler Feed Water System | NPSH on a running pump | 72 Ft | LO: < 60 Ft | NORMAL | 07/11/2026 07:04:56 | Mykhailenko, Eugene
Boiler Feed Water System | Boiler Feedwater Pump Running | B |  | NORMAL | 07/11/2026 07:05:49 | Mykhailenko, Eugene
Boiler Feed Water System | Lube Oil Temp of online BFWP (Highest) | 121 deg F | HI: > 146 deg F | NORMAL | 07/11/2026 07:06:10 | Mykhailenko, Eugene
Boiler Feed Water System | Standby BFWP in Auto | Yes |  | NORMAL | 07/11/2026 07:06:12 | Mykhailenko, Eugene
Boiler Feed Water System | Offline BFWP Lube oil pump running | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:12 | Mykhailenko, Eugene
Boiler Feed Water System | 01A BFP Min Flow recirc FCV-BFW147, IP discharge MOV-BFW139/140, HP discharge MOV-BFW145/146 are in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:14 | Mykhailenko, Eugene
Boiler Feed Water System | 01B BFP Min Flow recirc FCV-BFW187, IP discharge MOV-BFW179/80, HP discharge MOV-BFW185/186 are in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:15 | Mykhailenko, Eugene
Boiler Feed Water System | NPSH on a running pump | 77 Ft | LO: < 60 Ft | NORMAL | 07/11/2026 07:06:22 | Mykhailenko, Eugene
Auxiliary Steam | CRH to Aux Header PCV-CRG715 & PCV-CRH700 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:38 | Mykhailenko, Eugene
Auxiliary Steam | CRH To Aux Steam Attemp Block YV-BFW745 & TCV-BFW749 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:40 | Mykhailenko, Eugene
Auxiliary Steam | CRH To Aux Steam Attemp Block YV-BFW757 & TCV-BFW761 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:42 | Mykhailenko, Eugene
Auxiliary Steam | Auxiliary Electric Superheater in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:46 | Mykhailenko, Eugene
Auxiliary Steam | Aux steam crosstie valves are open MOV-AXS321/322 | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:48 | Mykhailenko, Eugene
Auxiliary Steam | CRH to Aux Header PCV-CRG715 & PCV-CRH700 in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:06:57 | Mykhailenko, Eugene
Auxiliary Steam | CRH To Aux Steam Attemp Block YV-BFW745 & TCV-BFW749 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:07:31 | Mykhailenko, Eugene
Auxiliary Steam | CRH To Aux Steam Attemp Block YV-BFW757 & TCV-BFW761 in Auto and Temp in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:07:35 | Mykhailenko, Eugene
Auxiliary Steam | Auxiliary Electric Superheater in Auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:07:38 | Mykhailenko, Eugene
Auxiliary Steam | Aux steam crosstie valves are open MOV-AXS321/322 | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:07:39 | Mykhailenko, Eugene
CRH system | ST Ventilation Valve Closed | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:07:54 | Mykhailenko, Eugene
CRH system | CRH Stm Bypass Desup Block YV-CND705 & TCV-CND706 in AUTO | Yes |  | NORMAL | 07/11/2026 07:07:55 | Mykhailenko, Eugene
CRH system | ST Ventilation Valve Closed | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:08:05 | Mykhailenko, Eugene
CRH system | CRH Stm Bypass Desup Block YV-CND705 & TCV-CND706 in AUTO | Yes |  | NORMAL | 07/11/2026 07:08:06 | Mykhailenko, Eugene
Drains | Blowdown Tank TCV-HBD901 & YV-SWS717 IN AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:08:28 | Mykhailenko, Eugene
Drains | HRSG Drain Sump Pumps In AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:08:33 | Mykhailenko, Eugene
Drains | HRSG Drain Sump Level | 4.4 Inches |  | NORMAL | 07/11/2026 07:08:52 | Mykhailenko, Eugene
Drains | HP Drains Tank Temp Cntrl TCV-CND717 in AUTO and Temperature in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:09:06 | Mykhailenko, Eugene
Drains | LP Drains Tank Temp Cntrl TCV-CND718 in AUTO and Temperature in range | Yes |  | NORMAL | 07/11/2026 07:09:09 | Mykhailenko, Eugene
Drains | HP Drains Tank Outlet Valve YV-STP131 & YV-STP132 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:09:11 | Mykhailenko, Eugene
Drains | LP Drains Tank Pump STP-PMP-01A & STP-PMP01B in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:09:13 | Mykhailenko, Eugene
Drains | Blowdown Tank TCV-HBD901 & YV-SWS717 IN AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:10:27 | Mykhailenko, Eugene
Drains | HRSG Drain Sump Pumps In AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:10:28 | Mykhailenko, Eugene
Drains | HRSG Drain Sump Level | 4.5 Inches |  | NORMAL | 07/11/2026 07:10:39 | Mykhailenko, Eugene
Drains | HP Drains Tank Temp Cntrl TCV-CND717 in AUTO and Temperature in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:09:29 | Mykhailenko, Eugene
Drains | LP Drains Tank Temp Cntrl TCV-CND718 in AUTO and Temperature in range | Yes |  | NORMAL | 07/11/2026 07:09:28 | Mykhailenko, Eugene
Drains | HP Drains Tank Outlet Valve YV-STP131 & YV-STP132 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:09:25 | Mykhailenko, Eugene
Drains | LP Drains Tank Pump STP-PMP-01A & STP-PMP01B in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:09:23 | Mykhailenko, Eugene
Condensate System | Demin Make-up LCV-DWS715 & YV-DWS719 In AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:10:53 | Mykhailenko, Eugene
Condensate System | Condensate Pumps Running | A; C |  | NORMAL | 07/11/2026 07:10:57 | Mykhailenko, Eugene
Condensate System | Condensate Reciever Tank Pressure | 3.8 inHg |  | NORMAL | 07/11/2026 07:11:07 | Mykhailenko, Eugene
Condensate System | Condensate Reciever Tank Temperature | 122 deg F | HI: > 150 deg F | NORMAL | 07/11/2026 07:11:15 | Mykhailenko, Eugene
Condensate System | CND TO HRSG CONTROL VLV PCV-CND455 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:11:23 | Mykhailenko, Eugene
Condensate System | Condensate Pump Min Flow Recirc FCV-CND331 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:11:25 | Mykhailenko, Eugene
Condensate System | Condensate Dump YV-CND441 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:11:27 | Mykhailenko, Eugene
Condensate System | Gland Steam Exhauster in Service | A |  | NORMAL | 07/11/2026 07:13:24 | Mykhailenko, Eugene
Condensate System | All condensate pumps are in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:11:36 | Mykhailenko, Eugene
Condensate System | Demin Make-up LCV-DWS715 & YV-DWS719 In AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:13:57 | Mykhailenko, Eugene
Condensate System | Condensate Pumps Running | A; B |  | NORMAL | 07/11/2026 07:14:01 | Mykhailenko, Eugene
Condensate System | Condensate Reciever Tank Pressure | 3.4 inHg |  | NORMAL | 07/11/2026 07:14:20 | Mykhailenko, Eugene
Condensate System | Condensate Reciever Tank Temperature | 119 deg F | HI: > 150 deg F | NORMAL | 07/11/2026 07:14:29 | Mykhailenko, Eugene
Condensate System | CND TO HRSG CONTROL VLV PCV-CND455 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:14:31 | Mykhailenko, Eugene
Condensate System | Condensate Pump Min Flow Recirc FCV-CND331 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:14:34 | Mykhailenko, Eugene
Condensate System | Condensate Dump YV-CND441 in AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:14:38 | Mykhailenko, Eugene
Condensate System | Gland Steam Exhauster in Service | A |  | NORMAL | 07/11/2026 07:14:39 | Mykhailenko, Eugene
Condensate System | All condensate pumps are in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:14:47 | Mykhailenko, Eugene
Air Cooled Condenser | ACC Duct Pressure | 3.8 inHg | HI: > 8 inHg | NORMAL | 07/11/2026 07:15:28 | Mykhailenko, Eugene
Air Cooled Condenser | Control Mode Selected by Operator | Pressure Control |  | NORMAL | 07/11/2026 07:15:30 | Mykhailenko, Eugene
Air Cooled Condenser | ACC Duct Saturated Temp | 123 deg F |  | NORMAL | 07/11/2026 07:15:40 | Mykhailenko, Eugene
Air Cooled Condenser | ACC Duct Pressure | 3.3 inHg | HI: > 8 inHg | NORMAL | 07/11/2026 07:15:59 | Mykhailenko, Eugene
Air Cooled Condenser | Control Mode Selected by Operator | Pressure Control |  | NORMAL | 07/11/2026 07:16:01 | Mykhailenko, Eugene
Air Cooled Condenser | ACC Duct Saturated Temp | 118 deg F |  | NORMAL | 07/11/2026 07:16:13 | Mykhailenko, Eugene
Air Removal System | Vacuum Pumps Running | B |  | NORMAL | 07/11/2026 07:16:53 | Mykhailenko, Eugene
Air Removal System | Seal Water Temperature on Running Pump | 109 deg F | HI: > 155 deg F | NORMAL | 07/11/2026 07:17:04 | Mykhailenko, Eugene
Air Removal System | Glycol Fin fans Running | A; B; C; D; E |  | NORMAL | 07/11/2026 07:17:12 | Mykhailenko, Eugene
Air Removal System | Glycol Receiver Tank Level | 57 Inches | LO: < 35 Inches | NORMAL | 07/11/2026 07:17:16 | Mykhailenko, Eugene
Air Removal System | ACC VAC GLYCOL Pump Running | A; B |  | NORMAL | 07/11/2026 07:17:20 | Mykhailenko, Eugene
Air Removal System | Vacuum Pumps Running | A |  | NORMAL | 07/11/2026 07:17:50 | Mykhailenko, Eugene
Air Removal System | Seal Water Temperature on Running Pump | 106 deg F | HI: > 155 deg F | NORMAL | 07/11/2026 07:18:00 | Mykhailenko, Eugene
Air Removal System | Glycol Fin fans Running | A; B; C; D; E |  | NORMAL | 07/11/2026 07:17:42 | Mykhailenko, Eugene
Air Removal System | Glycol Receiver Tank Level | 55 Inches | LO: < 35 Inches | NORMAL | 07/11/2026 07:17:39 | Mykhailenko, Eugene
Air Removal System | ACC VAC GLYCOL Pump Running | A; B |  | NORMAL | 07/11/2026 07:17:37 | Mykhailenko, Eugene
CCW | Closed Cooling WATER Pump In Service | B |  | NORMAL | 07/11/2026 07:18:09 | Mykhailenko, Eugene
CCW | ACHE Bypass temp Control TCV-CCW181 In AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:18:24 | Mykhailenko, Eugene
CCW | Closed Cooling Water Pump Recirc PCV-CCW-191 In AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:18:26 | Mykhailenko, Eugene
CCW | Closed Cooling Water Head Tank Level | 72 Inches | LO: < 36 Inches | NORMAL | 07/11/2026 07:18:19 | Mykhailenko, Eugene
CCW | Closed Cooling WATER Pump In Service | A |  | NORMAL | 07/11/2026 07:18:47 | Mykhailenko, Eugene
CCW | ACHE Bypass temp Control TCV-CCW181 In AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:18:49 | Mykhailenko, Eugene
CCW | Closed Cooling Water Pump Recirc PCV-CCW-191 In AUTO | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:18:54 | Mykhailenko, Eugene
CCW | Closed Cooling Water Head Tank Level | 75 Inches | LO: < 36 Inches | NORMAL | 07/11/2026 07:18:58 | Mykhailenko, Eugene
Sampling Analysis | U1 Water and Steam Chemistry in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:19:24 | Mykhailenko, Eugene
Sampling Analysis | U2 Water and Steam Chemistry in range | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:19:25 | Mykhailenko, Eugene
Turbine bearings | Highest Vibration | 5.4 |  | NORMAL | 07/11/2026 07:21:17 | Mykhailenko, Eugene
Turbine bearings | Highest bearing metal temp | 198 deg F | HI: > 210 deg F | NORMAL | 07/11/2026 07:21:24 | Mykhailenko, Eugene
Turbine bearings | Highest Oil Drain temperature | 159 deg F | HI: > 165 deg F | NORMAL | 07/11/2026 07:21:34 | Mykhailenko, Eugene
Control Oil System | Oil System Active alarms | No | HI: <> No | NORMAL | 07/11/2026 07:21:45 | Mykhailenko, Eugene
Control Oil System | Oil Pump running | B |  | NORMAL | 07/11/2026 07:21:47 | Mykhailenko, Eugene
Control Oil System | Oil Pumps and Heaters in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:21:50 | Mykhailenko, Eugene
Lube Oil System | Oil System Active alarms | Yes | HI: <> No | PENDING | 07/11/2026 07:21:57 | Mykhailenko, Eugene | Lube oil level low
Lube Oil System | Oil Pump running | B |  | NORMAL | 07/11/2026 07:22:29 | Mykhailenko, Eugene
Lube Oil System | Jacking Oil Pumps in auto | Yes |  | NORMAL | 07/11/2026 07:22:35 | Mykhailenko, Eugene
Lube Oil System | Vapor Extractors are in auto and 1 running | Yes |  | NORMAL | 07/11/2026 07:22:36 | Mykhailenko, Eugene
Lube Oil System | Oil Pumps and Heaters in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:22:37 | Mykhailenko, Eugene
Lube Oil System | Lube oil Temp after cooler | 114 deg F | HI: > 130 deg F | NORMAL | 07/11/2026 07:22:45 | Mykhailenko, Eugene
Lube Oil System | Turning Gear is in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:22:47 | Mykhailenko, Eugene
Seal Oil System | Seal Oil DP | 8.6 psi | HI: > 9.5 psi LO: < 7.5 psi | NORMAL | 07/11/2026 07:22:59 | Mykhailenko, Eugene
Seal Oil System | H2 purity | 99.9 % | LO: < 95 % | NORMAL | 07/11/2026 07:23:04 | Mykhailenko, Eugene
Seal Oil System | H2 pressure | 40.7 psig | HI: > 45 psig LO: < 38 psig | NORMAL | 07/11/2026 07:23:14 | Mykhailenko, Eugene
Seal Oil System | Oil System Active alarms | No | HI: <> No | NORMAL | 07/11/2026 07:23:16 | Mykhailenko, Eugene
Enhanced Cooling Air System | ECA compressor Running | Both |  | NORMAL | 07/11/2026 07:23:26 | Mykhailenko, Eugene
Enhanced Cooling Air System | ECA system active alarms | No | HI: <> No | NORMAL | 07/11/2026 07:23:27 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (A) Enclosure vent fan running (A) or (B) | A |  | NORMAL | 07/11/2026 07:23:54 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (A) vapor extractor running (A) or (B) | A |  | NORMAL | 07/11/2026 07:23:54 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (A) lube oil supply temp? < 165 alarms | 125 deg F | HI: > 155 deg F | NORMAL | 07/11/2026 07:23:57 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (A) lube oil reservoir Level | 10.5 inches |  | NORMAL | 07/11/2026 07:24:03 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (B) Enclosure vent fan running (A) or (B) | A |  | NORMAL | 07/11/2026 07:24:29 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (B) vapor extractor running (A) or (B) | A |  | NORMAL | 07/11/2026 07:24:30 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (B) lube oil supply temp? < 165alarm | 127 deg F | HI: > 155 deg F | NORMAL | 07/11/2026 07:24:38 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (B) lube oil reservoir level | 10.3 inches |  | NORMAL | 07/11/2026 07:24:45 | Mykhailenko, Eugene
2C/ECA Cooler Cooling water system | GT 2C/ECA cooler cooling water recirc pump running (A) or (B) | B |  | NORMAL | 07/11/2026 07:24:55 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | GT Package Vent Fan Running (A) or (B) | A |  | NORMAL | 07/11/2026 07:25:05 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | Evap Coolers in service? | Yes |  | NORMAL | 07/11/2026 07:25:07 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | Inlet Air Filter Inner Pressure? < -6 inH2O alarm | -3.45 inH2O | LO: < -6 inH2O | NORMAL | 07/11/2026 07:25:10 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | Anti-Icing Air Temp Control Vlvs In AUTO? | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:25:11 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | GT inlet air filter DP | 1.15 |  | NORMAL | 07/11/2026 07:25:17 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | GT Hepa Filter DP | 1.44 |  | NORMAL | 07/11/2026 07:25:18 | Mykhailenko, Eugene
Generator | Stator Coil Temp U/V/W Phase Highest Temp? < 235 alarms | 163 deg F | HI: > 200 deg F | NORMAL | 07/11/2026 07:25:35 | Mykhailenko, Eugene
Generator | Collector Housing Space Heater in AUTO? | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:25:37 | Mykhailenko, Eugene
Generator | Generator AVR and PSS mod on | Yes |  | NORMAL | 07/11/2026 07:25:37 | Mykhailenko, Eugene
Turbine bearings | Highest Vibration | 4 |  | NORMAL | 07/11/2026 07:27:20 | Mykhailenko, Eugene
Turbine bearings | Highest bearing metal temp | 186 deg F | HI: > 210 deg F | NORMAL | 07/11/2026 07:27:47 | Mykhailenko, Eugene
Turbine bearings | Highest Oil Drain temperature | 159 deg F | HI: > 165 deg F | NORMAL | 07/11/2026 07:27:59 | Mykhailenko, Eugene
Control Oil System | Oil System Active alarms | No | HI: <> No | NORMAL | 07/11/2026 07:28:25 | Mykhailenko, Eugene
Control Oil System | Oil Pump running | A |  | NORMAL | 07/11/2026 07:28:28 | Mykhailenko, Eugene
Control Oil System | Oil Pumps and Heaters in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:28:29 | Mykhailenko, Eugene
Lube Oil System | Oil System Active alarms | No | HI: <> No | NORMAL | 07/11/2026 07:28:44 | Mykhailenko, Eugene
Lube Oil System | Oil Pump running | A |  | NORMAL | 07/11/2026 07:29:16 | Mykhailenko, Eugene
Lube Oil System | Jacking Oil Pumps in auto | Yes |  | NORMAL | 07/11/2026 07:29:31 | Mykhailenko, Eugene
Lube Oil System | Vapor Extractors are in auto and 1 running | Yes |  | NORMAL | 07/11/2026 07:29:48 | Mykhailenko, Eugene
Lube Oil System | Oil Pumps and Heaters in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:29:50 | Mykhailenko, Eugene
Lube Oil System | Lube oil Temp after cooler | 114 deg F | HI: > 130 deg F | NORMAL | 07/11/2026 07:29:57 | Mykhailenko, Eugene
Lube Oil System | Turning Gear is in auto | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:29:59 | Mykhailenko, Eugene
Seal Oil System | Seal Oil DP | 8.8 psi | HI: > 9.5 psi LO: < 7.5 psi | NORMAL | 07/11/2026 07:30:08 | Mykhailenko, Eugene
Seal Oil System | H2 purity | 100 % | LO: < 95 % | NORMAL | 07/11/2026 07:30:20 | Mykhailenko, Eugene
Seal Oil System | H2 pressure | 40.3 psig | HI: > 45 psig LO: < 38 psig | NORMAL | 07/11/2026 07:30:29 | Mykhailenko, Eugene
Seal Oil System | Oil System Active alarms | No | HI: <> No | NORMAL | 07/11/2026 07:30:31 | Mykhailenko, Eugene
Enhanced Cooling Air System | ECA compressor Running | Both |  | NORMAL | 07/11/2026 07:30:47 | Mykhailenko, Eugene
Enhanced Cooling Air System | ECA system active alarms | No | HI: <> No | NORMAL | 07/11/2026 07:31:22 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (A) Enclosure vent fan running (A) or (B) | A |  | NORMAL | 07/11/2026 07:31:43 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (A) vapor extractor running (A) or (B) | A |  | NORMAL | 07/11/2026 07:31:44 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (A) lube oil supply temp? < 165 alarms | 140 deg F | HI: > 155 deg F | NORMAL | 07/11/2026 07:31:48 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (A) lube oil reservoir Level | 10.4 inches |  | NORMAL | 07/11/2026 07:31:55 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (B) Enclosure vent fan running (A) or (B) | A |  | NORMAL | 07/11/2026 07:32:11 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (B) vapor extractor running (A) or (B) | A |  | NORMAL | 07/11/2026 07:32:13 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (B) lube oil supply temp? < 165alarm | 139 deg F | HI: > 155 deg F | NORMAL | 07/11/2026 07:32:46 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT ECA Compressor (B) lube oil reservoir level | 10.67 inches |  | NORMAL | 07/11/2026 07:32:49 | Mykhailenko, Eugene
Enhanced Cooling Air System | GT 2C/ECA cooler cooling water recirc pump running (A) or (B) | A |  | NORMAL | 07/11/2026 07:33:04 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | GT Package Vent Fan Running (A) or (B) | A |  | NORMAL | 07/11/2026 07:33:12 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | Evap Coolers in service? | Yes |  | NORMAL | 07/11/2026 07:33:15 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | Inlet Air Filter Inner Pressure? < -6 inH2O alarm | -3.58 inH2O | LO: < -6 inH2O | NORMAL | 07/11/2026 07:33:32 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | Anti-Icing Air Temp Control Vlvs In AUTO? | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:33:35 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | GT inlet air filter DP | 1.11 |  | NORMAL | 07/11/2026 07:33:44 | Mykhailenko, Eugene
Air and Flue Gas System Diagram | GT Hepa Filter DP | 1.52 |  | NORMAL | 07/11/2026 07:33:47 | Mykhailenko, Eugene
Generator | Stator Coil Temp U/V/W Phase Highest Temp? < 235 alarms | 162 deg F | HI: > 200 deg F | NORMAL | 07/11/2026 07:34:07 | Mykhailenko, Eugene
Generator | Collector Housing Space Heater in AUTO? | Yes | HI: <> Yes | NORMAL | 07/11/2026 07:34:11 | Mykhailenko, Eugene
Generator | Generator AVR and PSS mod on | Yes |  | NORMAL | 07/11/2026 07:34:12 | Mykhailenko, Eugene