## First Sheet
Loc/Asset | Label | Last Response | Alarm Config | Condition | Response Date/Time | Response By | Comment | Active
ANSWER FIRST | Which Shift | Day |  | NORMAL | 07/11/2026 08:16:13 | Martinez, Geovanny
UNIT 1 | U1 Status? | Unit online; |  | NORMAL | 07/11/2026 08:16:13 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 01A (01-CCW-FAN-01A) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:20 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 01B (01-CCW-FAN-01B) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:20 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 01C (01-CCW-FAN-01C) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:16 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 02A (01-CCW-FAN-02A) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:17 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 02B (01-CCW-FAN-02B) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:19 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 02C (01-CCW-FAN-02C) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:25 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 03A (01-CCW-FAN-03A) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:25 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 03B (01-CCW-FAN-03B) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:18 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 03C (01-CCW-FAN-03C) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:23 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 04A (01-CCW-FAN-04A) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:24 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 04B (01-CCW-FAN-04B) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:18 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 04C (01-CCW-FAN-04C) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:20 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 05A (01-CCW-FAN-05A) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:27 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 05B (01-CCW-FAN-05B) | Fan condition (sound, vibration, cleanness) | Unsat |  | NORMAL | 07/11/2026 08:16:27 | Martinez, Geovanny
AIR COOLED HEAT EXCHANGER FAN 05C (01-CCW-FAN-05C) | Fan condition (sound, vibration, cleanness) | Sat |  | NORMAL | 07/11/2026 08:16:16 | Martinez, Geovanny
CLOSED COOLING WATER | CCW Pump Oil Level | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:28 | Martinez, Geovanny
CLOSED COOLING WATER | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:29 | Martinez, Geovanny
GT TCA COOLER 01MBH05AC301 (01MBH05AC301) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:30 | Martinez, Geovanny
GT2C/ECA COOLER COOLING WATER RECIRULATION PUMP A (LCA14AP101) | Recirc Cooling Pump Oil Level | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:37 | Martinez, Geovanny
GT2C/ECA COOLER COOLING WATER RECIRULATION PUMP A (LCA14AP101) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:38 | Martinez, Geovanny
ENHANCED COOLING AIR | ECA Compressor "A" Oil Level is in range and no leaks present | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:39 | Martinez, Geovanny
ENHANCED COOLING AIR | ECA Compressor "B" Oil Level is in range and no leaks present | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:39 | Martinez, Geovanny
SCR skid | Abnormal Conditions/Leaks | Sat | HI: <> Sat | NORMAL | 07/11/2026 08:16:41 | Martinez, Geovanny
SCR skid | SCR Fan "A" oil level | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:41 | Martinez, Geovanny
SCR skid | SCR Fan "B" oil level | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:42 | Martinez, Geovanny
SCR skid | Ammonia injection strainer DP | 1 psi | HI: > 5 psi | NORMAL | 07/11/2026 08:16:42 | Martinez, Geovanny
HRSG | HRSG Sump Control Panel/Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:44 | Martinez, Geovanny
HRSG | Visual Steam/Water Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:44 | Martinez, Geovanny
UNIT 1 CHEM SHACK (01-CHEMSHACK) | Building Temperature | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:45 | Martinez, Geovanny
UNIT 1 CHEM SHACK (01-CHEMSHACK) | Ammonia Pump Discharge Pressure | 650 |  | NORMAL | 07/11/2026 08:16:46 | Martinez, Geovanny
UNIT 1 CHEM SHACK (01-CHEMSHACK) | Ammonia pump drawdown | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:46 | Martinez, Geovanny
UNIT 1 CHEM SHACK (01-CHEMSHACK) | Ammonia Tote Level | 21 INCHES |  | NORMAL | 07/11/2026 08:16:48 | Martinez, Geovanny
UNIT 1 CHEM SHACK (01-CHEMSHACK) | Check Skid Display | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:49 | Martinez, Geovanny
UNIT 1 CHEM SHACK (01-CHEMSHACK) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 08:16:50 | Martinez, Geovanny
UNIT 1 | Chemical Injection Pumps are off and system is ready for start. | Yes | HI: <> Yes | NORMAL | 06/24/2026 18:36:11 | Silva, Juan
UNIT 1 SAMPLE PANEL (00-EWS-PWS620F) | Check Resin Columns | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:05:30 | Martinez, Geovanny
UNIT 1 SAMPLE PANEL (00-EWS-PWS620F) | Make Sure Samples are Flowing | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:05:33 | Martinez, Geovanny
UNIT 1 SAMPLE PANEL (00-EWS-PWS620F) | Sample Temps are in Range | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:05:34 | Martinez, Geovanny
UNIT 1 SAMPLE PANEL (00-EWS-PWS620F) | TCU Display: Temp (76F) Pump Pressure (35-45psig) | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:05:34 | Martinez, Geovanny
UNIT 1 SAMPLE PANEL (00-EWS-PWS620F) | Sample System is in flush and ready for start. | Yes | HI: <> Yes | NORMAL | 06/24/2026 18:34:19 | Silva, Juan
BOILER FEEDWATER PUMP 1A (01-BFW-PMP-01A) | Motor Oil Levels/Flow SG | Sat | LO: = Unsat | NORMAL | 07/11/2026 09:05:35 | Martinez, Geovanny
BOILER FEEDWATER PUMP 1A (01-BFW-PMP-01A) | CCW Temp Differential (In/out) is less then 10F | 0 Deg. F | HI: > 10 Deg. F | NORMAL | 07/11/2026 09:05:36 | Martinez, Geovanny
BOILER FEEDWATER PUMP MOTOR 1A (01-BFW-MPM-01A) | BFP A Motor Cooling Air Screen Clean | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:05:36 | Martinez, Geovanny
BOILER FEEDWATER PUMP 1B (01-BFW-PMP-01B) | Motor Oil Levels/Flow SG | Sat | LO: = Unsat | NORMAL | 07/11/2026 09:05:37 | Martinez, Geovanny
BOILER FEEDWATER PUMP 1B (01-BFW-PMP-01B) | CCW Temp Differential (In/out) is less then 10F | 10 Deg. F | HI: > 10 Deg. F | NORMAL | 07/11/2026 09:05:37 | Martinez, Geovanny
BOILER FEEDWATER PUMP MOTOR 1A (01-BFW-MPM-01A) | BFP B Motor Cooling Air Screen Clean | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:05:38 | Martinez, Geovanny
UNIT 1 HRSG MCC 111 (01-HRG-MCC-111) | Building Temperature | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:05:39 | Martinez, Geovanny
HRSG DUCT BURNER FUEL SKID 01-FGS-SKD-03 (01-FGS-SKD-03) | Enclosure Pressure Ok | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:06:23 | Martinez, Geovanny
SCANNER BLOWER (01-SCANNERBLOWER) | Discharge Pressure | 46 inH20 |  | NORMAL | 07/11/2026 09:06:23 | Martinez, Geovanny
HRSG DUCT BURNER FUEL SKID 01-FGS-SKD-03 (01-FGS-SKD-03) | Check Display Screen/Alarms | Sat | HI: = Unsat | NORMAL | 11/17/2023 18:50:53 | Stroud, Andrew
FUEL GAS PERFORMANCE HEATER 01-FGS-HEX-01 (01-FGS-HEX-01) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:06:25 | Martinez, Geovanny
FIRE PROTECTION SYSTEM | Tank Pressure (290-310) | 300 | HI: > 310 LO: < 290 | NORMAL | 07/11/2026 09:10:47 | Martinez, Geovanny
FIRE PROTECTION SYSTEM | Tank Level % (>50%) | 80 % | LO: < 50 % | NORMAL | 07/11/2026 09:10:47 | Martinez, Geovanny
FIRE PROTECTION SYSTEM | Alarms | No | HI: = Yes | NORMAL | 07/11/2026 09:10:48 | Martinez, Geovanny
GAS TURBINE | Are isolation valves open? | Yes |  | NORMAL | 07/11/2026 09:10:48 | Martinez, Geovanny
GAS TURBINE | All streets have 112 gpm flow? | Yes |  | NORMAL | 07/11/2026 09:10:50 | Martinez, Geovanny
UNIT 1 EXCITOR ROOM (01-EXCITOR) | Active Alarms | No | HI: <> No | NORMAL | 07/11/2026 09:10:51 | Martinez, Geovanny
UNIT 1 EXCITOR ROOM (01-EXCITOR) | Building Temperature (65-85 F) | Sat | HI: > 85 LO: < 65 | NORMAL | 07/11/2026 09:10:51 | Martinez, Geovanny
UNIT 1 EXCITOR ROOM (01-EXCITOR) | Check Cubicle Filters | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:10:52 | Martinez, Geovanny
U1 SFC TRANSFORMER (52-11-04B) | SFC Alarms on Display Screen | No | HI: = Yes | NORMAL | 07/11/2026 09:10:53 | Martinez, Geovanny
U1 SFC TRANSFORMER (52-11-04B) | Building Temp (65-85 F) | Sat | HI: <> Sat | NORMAL | 07/11/2026 09:10:54 | Martinez, Geovanny
ST DRAINS TANK SUMP PUMP 1A 01-PDR-PMP-01A (01-PDR-PMP-01A) | Sump free of Water | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:10:57 | Martinez, Geovanny
ST DRAINS TANK SUMP PUMP 1A 01-PDR-PMP-01A (01-PDR-PMP-01A) | LP Drains Tank Pump Seal Water Pressure | 20 |  | NORMAL | 07/11/2026 09:10:59 | Martinez, Geovanny
ST DRAINS TANK SUMP PUMP 1A 01-PDR-PMP-01A (01-PDR-PMP-01A) | ST Drains Sump Pump Panel/Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:11:01 | Martinez, Geovanny
CONDENSATE | Motor Oil Levels | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:11:03 | Martinez, Geovanny
CONDENSATE | Pump Seal Water flow | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:11:04 | Martinez, Geovanny
CONDENSATE | Motor Cooling Air Screens Clean | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:11:04 | Martinez, Geovanny
CONDENSATE | Electrical Box Desiccant is Blue | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:11:05 | Martinez, Geovanny
CONDENSATE | Abnormal Conditions/Leaks | Unsat | HI: = Unsat | PENDING | 07/11/2026 09:11:06 | Martinez, Geovanny
SEAL OIL VACUUM PUMP (A) (01-MKV05AP201) | Separator Tank (50%) | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:11:26 | Martinez, Geovanny
SEAL OIL VACUUM PUMP (A) (01-MKV05AP201) | Seal Water Temperature on running pumps (40-150 F) | 98 Deg F | HI: > 150 Deg F LO: < 40 Deg F | NORMAL | 07/11/2026 09:11:29 | Martinez, Geovanny
ACC | ACC 1A (oil level/desiccant/other abnormal conditions) | Unsat |  | NORMAL | 07/10/2026 09:11:27 | Martinez, Geovanny | Needs new Desiccant. Will replace on tomorrows rounds.
ACC | ACC 1B (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:32 | Martinez, Geovanny
ACC | ACC 1C (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:32 | Martinez, Geovanny
ACC | ACC 1D (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:33 | Martinez, Geovanny
ACC | ACC 1E (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:33 | Martinez, Geovanny
ACC | ACC 1F (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:34 | Martinez, Geovanny
ACC | ACC 2A (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:34 | Martinez, Geovanny
ACC | ACC 2B (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:35 | Martinez, Geovanny
ACC | ACC 2C (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:35 | Martinez, Geovanny
ACC | ACC 2D (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:36 | Martinez, Geovanny
ACC | ACC 2E (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:37 | Martinez, Geovanny
ACC | ACC 2F (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:37 | Martinez, Geovanny
ACC | ACC 3A (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:38 | Martinez, Geovanny
ACC | ACC 3B (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:38 | Martinez, Geovanny
ACC | ACC 3C (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:38 | Martinez, Geovanny
ACC | ACC 3D (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:39 | Martinez, Geovanny
ACC | ACC 3E (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:40 | Martinez, Geovanny
ACC | ACC 3F (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:41 | Martinez, Geovanny
ACC | ACC 4A (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:41 | Martinez, Geovanny
ACC | ACC 4B (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:41 | Martinez, Geovanny
ACC | ACC 4C (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:42 | Martinez, Geovanny
ACC | ACC 4D (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:42 | Martinez, Geovanny
ACC | ACC 4E (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:43 | Martinez, Geovanny
ACC | ACC 4F (oil level/desiccant/other abnormal conditions) | Sat |  | NORMAL | 07/10/2026 09:11:44 | Martinez, Geovanny
ACC MCC (01-ACC-MCC) | Building Temperature (65-85 F) | Sat | HI: <> Sat | NORMAL | 07/11/2026 09:11:43 | Martinez, Geovanny
C02 TANK HEATER (SGJ02AH001) | CO2 Mini Bulk Tank Level (Order at <70%) | 95 % | LO: < 70 % | NORMAL | 07/11/2026 09:12:17 | Martinez, Geovanny
C02 TANK HEATER (SGJ02AH001) | CO2 Mini Bulk Tank Pressure | 270 |  | NORMAL | 07/11/2026 09:12:17 | Martinez, Geovanny
GRAVEL/CALCITE TANK 6A 01-DWS-TNK-06A (01-DWS-TNK-06A) | Check Display, Note any Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:12:20 | Martinez, Geovanny
GAS TURBINE | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:12:22 | Martinez, Geovanny
STEAM TURBINE | Electric SPH PLC Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:17 | Martinez, Geovanny
STEAM TURBINE | Water in Basement | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:17 | Martinez, Geovanny
STEAM TURBINE | #7 Bearing Area Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:17 | Martinez, Geovanny
GLAND STEAM CONDENSER 01-MAW01AC101 (01-MAW01AC101) | Level in SG (about 1 inch) | Sat |  | NORMAL | 07/11/2026 09:13:19 | Martinez, Geovanny
GLAND STEAM CONDENSER 01-MAW01AC101 (01-MAW01AC101) | Turning Gear Oil Level | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:20 | Martinez, Geovanny
GLAND STEAM CONDENSER 01-MAW01AC101 (01-MAW01AC101) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:20 | Martinez, Geovanny
SEAL OIL | Seal Oil/H2 DP (8 PSI) | 8.5 PSI | HI: > 9 PSI LO: < 7.8 PSI | NORMAL | 07/11/2026 09:13:26 | Martinez, Geovanny
SEAL OIL | Discharge Filter DP | 2.4 | HI: = Unsat | NORMAL | 07/11/2026 09:13:28 | Martinez, Geovanny
SEAL OIL | Vacuum Tank Level/float trap level (50%) | Sat | HI: = Unsat | NORMAL | 07/10/2026 07:10:03 | Martinez, Geovanny
SEAL OIL | Vacuum tank pressure | -14.4 |  | NORMAL | 07/11/2026 09:13:33 | Martinez, Geovanny
SEAL OIL | Seal oil pump discharge pressure | 83 |  | NORMAL | 07/11/2026 09:13:34 | Martinez, Geovanny
SEAL OIL | Vacuum Pumps oil levels | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:35 | Martinez, Geovanny
GENERATOR | H2 Pressure (40-42 PSIG) | 41 PSIG | HI: > 44 PSIG LO: < 39 PSIG | NORMAL | 07/11/2026 09:13:47 | Martinez, Geovanny
GENERATOR | Hydrogen Purity >95% | 99.9 % | LO: < 95 % | NORMAL | 07/11/2026 09:13:36 | Martinez, Geovanny
GENERATOR | Hydrogen flow to purity meter (500) | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:37 | Martinez, Geovanny
HYDROGEN GAS DRYER (MKG03AT001) | Check Display, Note any Alarms | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:49 | Martinez, Geovanny
HYDROGEN GAS DRYER (MKG03AT001) | Dryer Desiccant Indicator | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:13:49 | Martinez, Geovanny
CONTROL OIL | Local pressure gauge readings = pressure indicating transmitter. | Yes | HI: = No | NORMAL | 07/11/2026 09:14:02 | Martinez, Geovanny
CONTROL OIL | Polishing Filter Button Indicator | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:14:03 | Martinez, Geovanny
CONTROL OIL | Tank Temperature | 114 | HI: > 130 LO: < 90 | NORMAL | 07/11/2026 09:14:05 | Martinez, Geovanny
CONTROL OIL | Tank Level Normal | 10 Inches | HI: = Unsat Inches | NORMAL | 07/11/2026 09:14:06 | Martinez, Geovanny
CONTROL OIL | Is nitrogen flow meter reading 30 SCFH? | Yes | HI: = No | NORMAL | 07/11/2026 09:14:06 | Martinez, Geovanny
JACKING OIL | Outlet Pressure (2442 PSIG) | 2250 PSIG |  | NORMAL | 06/24/2026 18:25:43 | Silva, Juan
JACKING OIL | Filter DP Button Indicator | Sat | HI: = Unsat | NORMAL | 06/24/2026 18:25:43 | Silva, Juan
LUBE OIL | Reservoir Level | 35 | LO: < 30 | NORMAL | 07/11/2026 09:14:09 | Martinez, Geovanny
LUBE OIL | Reservoir Temperature | 144 |  | NORMAL | 07/11/2026 09:14:10 | Martinez, Geovanny
LUBE OIL | Main Lube Oil Pressure (25 PSIG) | 27 PSIG |  | NORMAL | 07/11/2026 09:14:11 | Martinez, Geovanny
LUBE OIL | Mist Eliminator Vacuum (-10 inH20) | -9 inH20 | HI: > -8 inH20 LO: < -12 inH20 | NORMAL | 07/11/2026 09:14:11 | Martinez, Geovanny
LUBE OIL | Purifier DP | 1.8 |  | NORMAL | 07/11/2026 09:14:13 | Martinez, Geovanny
LUBE OIL | Purifier Tank Level SG | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:14:14 | Martinez, Geovanny
LUBE OIL | Lube Oil Mist Eliminator DP | 16 |  | NORMAL | 07/11/2026 09:14:16 | Martinez, Geovanny
GT 2C COOLER 01MBH04AC201 (01MBH04AC201) | Abnormal Conditions/Leaks | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:14:18 | Martinez, Geovanny
TCP (01-TCP) | Building Temperature | 69 |  | NORMAL | 07/11/2026 09:15:26 | Martinez, Geovanny
TCP (01-TCP) | Battery Room Vent Fan On | Yes |  | NORMAL | 07/11/2026 09:15:27 | Martinez, Geovanny
TCP (01-TCP) | Benning display Check and Volts | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:15:29 | Martinez, Geovanny
TCP (01-TCP) | Gutor Display and Volts | Sat | HI: = Unsat | NORMAL | 07/11/2026 09:15:28 | Martinez, Geovanny